## General Su...y Report - FLAT-31
General Summary Report
CYMCAP Version |  | 9.0 1 Revision
Study: |  | flat
Execution: |  | smoketest_multi_backfill_regression
Date: |  | 2026-01-01 00:00:00
Simulation Data
Installation type: |  | Multiple Ductbanks
Steady State Option |  | Temperature
Ambient temperature [°C] |  | 30
Native Soil Thermal Resistivity [K.m/W] |  | 1.36
Consider Non-Isothermal Earth Surface |  | No
Consider effect of soil dry out |  | No
Consider Electrical interaction between circuits |  | No
Induced current in metallic layers as a fraction of conductor current (applied to all single phase circuits) [A] |  | 0
Installation Type:Multiple Ductbanks/Backfills
Ambient Soil Temperature at Installation Depth [°C] |  | 30
Native Soil Thermal Resistivity [K.m/W] |  | 1.36
Consider Non-Isothermal Earth Surface |  | No
Layer Name |  | X [m] | Y [m] | Width [m] | Height [m] | Thermal Resistivity [K.m/W]
Backfill |  | 1.75 | 0.9 | 1.3 | 1 | 1
Backfill |  | -1.75 | 0.9 | 1.3 | 1 | 1
General Cable Information
Cable ID |  | Number of Cores | Conductor Construction | Voltage [kV] | Conductor Area [mm²] | Cable Overall Diameter [mm] | Maximum Steady-State Conductor Temperature [ºC] | Maximum Emergency Conductor Temperature [ºC]
1C132KV2000MM2CU |  | Single Core | 6 Segments | 132 | 2000 | 137.6 | 90 | 110
Detailed Cable Information
Cable ID |  | Conductor | Insulation | Sheath / Tape | Concentric Wires | Filler | Armour | Jacket / Armour Serving
1C132KV2000MM2CU |  | Copper | XLPE Unfilled | Aluminum | n/a | n/a | n/a | Polyethylene
General Input Data
Cable | Cable ID | Circuit No. | Phase | Fq [Hz] | X [m] | Y [m] | DLF [p.u.] | Sheath / Shield Bonding
Cable Index Number | Cable Equipment ID | Circuit No. | Cable Phase | Operating Frequency | X coordinate | Y coordinate | Daily Load Factor | Bonding Type
1 | 1C132KV2000MM2CU | 1 | A | 50 | 1.4 | 1.1588 | 1 | 1 Conductor 1 Point Bonded Flat
2 | 1C132KV2000MM2CU | 1 | B | 50 | 1.75 | 1.1588 | 1 | 1 Conductor 1 Point Bonded Flat
3 | 1C132KV2000MM2CU | 1 | C | 50 | 2.1 | 1.1588 | 1 | 1 Conductor 1 Point Bonded Flat
4 | 1C132KV2000MM2CU | 2 | A | 50 | -2.1 | 1.1588 | 1 | 1 Conductor 1 Point Bonded Flat
5 | 1C132KV2000MM2CU | 2 | B | 50 | -1.75 | 1.1588 | 1 | 1 Conductor 1 Point Bonded Flat
6 | 1C132KV2000MM2CU | 2 | C | 50 | -1.4 | 1.1588 | 1 | 1 Conductor 1 Point Bonded Flat
Ampacity and Temperatures
Cable | Cable ID | I [A] | θc [°C] | θs [°C] | θa [°C] | θsurf [°C] | θduct [°C] | θair / θcasing [°C]
Cable Index Number | Cable Equipment ID | Steady State Ampacity | Conductor temperature | Sheath/Shield temperature | Armour temperature | Cable surface temperature | Duct surface temperature | Mean air temperature in the tunnel / Casing surface temperature
1 | 1C132KV2000MM2CU | 1310 | 83.7916 | 72.0689 | n/a | 69.7894 | 62.4771 | n/a
2 | 1C132KV2000MM2CU | 1310 | 88.1938 | 76.332 | n/a | 73.703 | 65.384 | n/a
3 | 1C132KV2000MM2CU | 1310 | 82.9165 | 71.2212 | n/a | 68.9351 | 61.5772 | n/a
4 | 1C132KV2000MM2CU | 1310 | 82.8399 | 71.147 | n/a | 68.8729 | 61.5521 | n/a
5 | 1C132KV2000MM2CU | 1310 | 88.1987 | 76.3368 | n/a | 73.7077 | 65.3887 | n/a
6 | 1C132KV2000MM2CU | 1310 | 83.885 | 72.1592 | n/a | 69.8677 | 62.5186 | n/a
Electrical Resistances
Cable | Cable ID | R₀ [Ω/km] | ys | yp | R [Ω/km] | R's [Ω/km] | R'w [Ω/km] | R'a [Ω/km]
Cable Index Number | Cable Equipment ID | DC Resistance of the conductor at 20°C | Skin Effect Factor | Proximity Effect Factor | AC Resistance of Conductor at Operating Temperature | DC Resistance of Sheath at Operating Temperature | DC Resistance of Concentric Wires at Operating Temperature | DC Resistance of Armor at Operating Temperature
1 | 1C132KV2000MM2CU | 0.009 | 0.074762 | 0.0026247 | 0.012127 | 0.037558 | n/a | n/a
2 | 1C132KV2000MM2CU | 0.009 | 0.072854 | 0.0025609 | 0.012273 | 0.038091 | n/a | n/a
3 | 1C132KV2000MM2CU | 0.009 | 0.07515 | 0.0026377 | 0.012099 | 0.037452 | n/a | n/a
4 | 1C132KV2000MM2CU | 0.009 | 0.075184 | 0.0026389 | 0.012096 | 0.037443 | n/a | n/a
5 | 1C132KV2000MM2CU | 0.009 | 0.072851 | 0.0025608 | 0.012273 | 0.038092 | n/a | n/a
6 | 1C132KV2000MM2CU | 0.009 | 0.07472 | 0.0026234 | 0.01213 | 0.037569 | n/a | n/a
Thermal Resistances
Cable | Cable ID | T₁ [K.m/W] | T₂ [K.m/W] | T₃ [K.m/W] | T₄' [K.m/W] | T₄'' [K.m/W] | T₄''' [K.m/W] | T₄ [K.m/W]
Cable Index Number | Cable Equipment ID | Thermal resistance of insulation | Thermal resistance of bedding | Thermal resistance of outer covering | Thermal resistance inside the duct | Thermal resistance of the duct | Thermal resistance of the external medium | Total external thermal resistance
1 | 1C132KV2000MM2CU | 0.55629 | 0 | 0.10188 | 0.21435 | 0.11247 | 1.4517 | 1.7785
2 | 1C132KV2000MM2CU | 0.55629 | 0 | 0.10188 | 0.20993 | 0.11247 | 1.3712 | 1.6936
3 | 1C132KV2000MM2CU | 0.55629 | 0 | 0.10188 | 0.21545 | 0.11247 | 1.4074 | 1.7353
4 | 1C132KV2000MM2CU | 0.55629 | 0 | 0.10188 | 0.21551 | 0.11247 | 1.4137 | 1.7416
5 | 1C132KV2000MM2CU | 0.55629 | 0 | 0.10188 | 0.20993 | 0.11247 | 1.3714 | 1.6938
6 | 1C132KV2000MM2CU | 0.55629 | 0 | 0.10188 | 0.21426 | 0.11247 | 1.4459 | 1.7726
Losses
Cable | Cable ID | Wc [W/m] | Wd [W/m] | Ws [W/m] | Wa [W/m] | Wt [W/m] | ƛ₁ | ƛ₂
Cable Index Number | Cable Equipment ID | Conductor Losses | Dielectric Losses | Metallic Screen Losses | Armor/Pipe Losses | Total Losses | Screen Loss Factor | Armour Loss Factor + Pipe Loss Factor
1 | 1C132KV2000MM2CU | 20.8118 | 0.52341 | 1.0383 | 0 | 22.3735 | 0.049891 | 0
2 | 1C132KV2000MM2CU | 21.0611 | 0.52341 | 4.2188 | 0 | 25.8033 | 0.20031 | 0
3 | 1C132KV2000MM2CU | 20.7623 | 0.52341 | 1.1523 | 0 | 22.438 | 0.055499 | 0
4 | 1C132KV2000MM2CU | 20.758 | 0.52341 | 1.0391 | 0 | 22.3205 | 0.050058 | 0
5 | 1C132KV2000MM2CU | 21.0614 | 0.52341 | 4.2188 | 0 | 25.8036 | 0.20031 | 0
6 | 1C132KV2000MM2CU | 20.8171 | 0.52341 | 1.1514 | 0 | 22.4919 | 0.055311 | 0
Complementary Information
Cable | Cable ID | Δθint [°C] | [A] | [µF/km] | [Ω] | [Ω/km] | [Ω/km] | [V/A/km]
Cable Index Number | Cable Equipment ID | Temperature rise due to surrounding heat sources | Induced current on Metallic Screen | Cable Capacitance | Surge Impedance | Reactance of Conductor | Reactance of Metallic Sheath | Voltage drop for Three Phase System
1 | 1C132KV2000MM2CU | 19.5102 | 0 | 0.287 | 43.9635 | 0.17418 | 0.11514 | 0.021005
2 | 1C132KV2000MM2CU | 20.4261 | 0 | 0.287 | 43.9635 | 0.17418 | 0.11514 | 0.021257
3 | 1C132KV2000MM2CU | 18.5416 | 0 | 0.287 | 43.9635 | 0.17418 | 0.11514 | 0.020955
4 | 1C132KV2000MM2CU | 18.5768 | 0 | 0.287 | 43.9635 | 0.17418 | 0.11514 | 0.020951
5 | 1C132KV2000MM2CU | 20.4279 | 0 | 0.287 | 43.9635 | 0.17418 | 0.11514 | 0.021257
6 | 1C132KV2000MM2CU | 19.4795 | 0 | 0.287 | 43.9635 | 0.17418 | 0.11514 | 0.021011

## Study Summary - FLAT-31
Study Summary
CYMCAP Version |  | 9.0 1 Revision
Study: |  | flat
Execution: |  | smoketest_multi_backfill_regression
Date: |  | 2026-01-01 00:00:00
General Simulation Data
Steady State Option | [8 empty] | Temperature
Consider Electrical interaction between circuits | [8 empty] | No
Induced currents in metallic layers as a fraction of conductor current (applied to all single phase circuits) : | [8 empty] | 0
Conductor Resistances Computation Option: | [8 empty] | IEC-228
Standard Settings Options
General guidance | [8 empty] | Custom
Factor on RAC due to magnetic armour | [8 empty] | CIGREGuidance
Factor on RAC due to magnetic duct | [8 empty] | CIGREGuidance
Factor on ƛ₁ due to magnetic armour | [8 empty] | CYMCAPGuidance
Factor on ƛ₁ due to magnetic duct | [8 empty] | CIGREGuidance
Factor on ƛ₂ due to ƛ'₁ | [8 empty] | CYMCAPGuidance
ƛ''₁ computation | [8 empty] | CIGREGuidance
ƛ₂pipe computation | [8 empty] | CYMCAPGuidance
Wd computation | [8 empty] | CIGREGuidance
T₂ computation | [8 empty] | CIGREGuidance
T₄ computation | [8 empty] | CYMCAPGuidance
Installation Type:Multiple Ductbanks/Backfills
Ambient Soil Temperature at Installation Depth [°C] | [8 empty] | 30
Native Soil Thermal Resistivity [K.m/W] | [8 empty] | 1.36
Consider Non-Isothermal Earth Surface | [8 empty] | No
Layer Name |  | X [m] | Y [m] | Width [m] | Height [m] | Thermal Resistivity [K.m/W]
Backfill |  | 1.75 | 0.9 | 1.3 | 1 | 1
Backfill |  | -1.75 | 0.9 | 1.3 | 1 | 1
Results Summary
Cable No. | Cable ID | Circuit No. | Cable Phase | Cable Frequency | Daily Load Factor | X coordinate [m] | Y coordinate [m] | Conductor temperature [°C] | Ampacity [A]
1 | 1C132KV2000MM2CU | 1 | A | 50 | 1 | 1.4 | 1.1588 | 83.7916 | 1310
2 | 1C132KV2000MM2CU | 1 | B | 50 | 1 | 1.75 | 1.1588 | 88.1938 | 1310
3 | 1C132KV2000MM2CU | 1 | C | 50 | 1 | 2.1 | 1.1588 | 82.9165 | 1310
4 | 1C132KV2000MM2CU | 2 | A | 50 | 1 | -2.1 | 1.1588 | 82.8399 | 1310
5 | 1C132KV2000MM2CU | 2 | B | 50 | 1 | -1.75 | 1.1588 | 88.1987 | 1310
6 | 1C132KV2000MM2CU | 2 | C | 50 | 1 | -1.4 | 1.1588 | 83.885 | 1310

## Steady State Summary - FLAT-31
Steady State Summary
CYMCAP Version |  | 9.0 1 Revision
Study: |  | flat
Execution: |  | smoketest_multi_backfill_regression
Date: |  | 2026-01-01 00:00:00
Simulation Data
Installation type: |  | Multiple Ductbanks
Steady State Option |  | Temperature
Ambient temperature [°C] |  | 30
Native Soil Thermal Resistivity [K.m/W] |  | 1.36
Consider Non-Isothermal Earth Surface |  | No
Consider effect of soil dry out |  | No
Consider Electrical interaction between circuits |  | No
Induced current in metallic layers as a fraction of conductor current (applied to all single phase circuits) [A] |  | 0
Variable | Description |  | Unit | Cables
Cable No. | Cable Index Number |  |  | 1 | 2 | 3 | 4 | 5 | 6
General Input Data
Cable ID | Cable Equipment ID |  |  | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU
Circuit No. | Circuit No. |  |  | 1 | 1 | 1 | 2 | 2 | 2
Phase | Cable Phase |  |  | A | B | C | A | B | C
Fq | Operating Frequency |  | [Hz] | 50 | 50 | 50 | 50 | 50 | 50
X | X coordinate |  | [m] | 1.4 | 1.75 | 2.1 | -2.1 | -1.75 | -1.4
Y | Y coordinate |  | [m] | 1.1588 | 1.1588 | 1.1588 | 1.1588 | 1.1588 | 1.1588
DLF | Daily Load Factor |  | [p.u.] | bar: Cables 1 to Cables 6
| Bonding Type |  |  | 1 Conductor 1 Point Bonded Flat | 1 Conductor 1 Point Bonded Flat | 1 Conductor 1 Point Bonded Flat | 1 Conductor 1 Point Bonded Flat | 1 Conductor 1 Point Bonded Flat | 1 Conductor 1 Point Bonded Flat
Ampacity
I | Steady State Ampacity |  | [A] | 1310 | 1310 | 1310 | 1310 | 1310 | 1310
I₀ | Steady State Ampacity without insulation temperature drop constraint |  | [A] | n/a | n/a | n/a | n/a | n/a | n/a
Temperatures
θc | Conductor temperature |  | [°C] | 83.7916 | 88.1938 | 82.9165 | 82.8399 | 88.1987 | 83.885
Δθins | Temperature drop across the insulation |  | [°C] | n/a | n/a | n/a | n/a | n/a | n/a
θs | Sheath/Shield temperature |  | [°C] | 72.0689 | 76.332 | 71.2212 | 71.147 | 76.3368 | 72.1592
θa | Armour temperature |  | [°C] | n/a | n/a | n/a | n/a | n/a | n/a
θsurf | Cable surface temperature |  | [°C] | 69.7894 | 73.703 | 68.9351 | 68.8729 | 73.7077 | 69.8677
θduct | Duct surface temperature |  | [°C] | 62.4771 | 65.384 | 61.5772 | 61.5521 | 65.3887 | 62.5186
Resistances
R₀ | DC Resistance of the conductor at 20°C |  | [Ω/km] | 0.009 | 0.009 | 0.009 | 0.009 | 0.009 | 0.009
R | AC Resistance of the Conductor at Operating Temperature |  | [Ω/km] | 0.012127 | 0.012273 | 0.012099 | 0.012096 | 0.012273 | 0.01213
ys | Skin Effect Factor |  |  | 0.074762 | 0.072854 | 0.07515 | 0.075184 | 0.072851 | 0.07472
yp | Proximity Effect Factor |  |  | 0.0026247 | 0.0025609 | 0.0026377 | 0.0026389 | 0.0025608 | 0.0026234
Losses
Wc | Conductor Losses |  | [W/m] | 20.8118 | 21.0611 | 20.7623 | 20.758 | 21.0614 | 20.8171
Wd | Dielectric Losses |  | [W/m] | 0.52341 | 0.52341 | 0.52341 | 0.52341 | 0.52341 | 0.52341
Ws | Metallic Screen Losses |  | [W/m] | 1.0383 | 4.2188 | 1.1523 | 1.0391 | 4.2188 | 1.1514
Wa | Armor/Pipe Losses |  | [W/m] | 0 | 0 | 0 | 0 | 0 | 0
Wt | Total Losses |  | [W/m] | 22.3735 | 25.8033 | 22.438 | 22.3205 | 25.8036 | 22.4919
ƛ₁ | Screen Loss Factor |  |  | 0.049891 | 0.20031 | 0.055499 | 0.050058 | 0.20031 | 0.055311
ƛ₂ | Armour Loss Factor + Pipe Loss Factor |  |  | 0 | 0 | 0 | 0 | 0 | 0
Thermal resistances
T1 | Thermal Resistance Between Conductor and Screen |  | [K.m/W] | 0.55629 | 0.55629 | 0.55629 | 0.55629 | 0.55629 | 0.55629
T2 | Thermal Resistance Between Screen and Armour |  | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
T3 | Thermal Resistance of the Jacket/Pipe Coating |  | [K.m/W] | 0.10188 | 0.10188 | 0.10188 | 0.10188 | 0.10188 | 0.10188
T4 | Total external thermal resistance |  | [K.m/W] | 1.7785 | 1.6936 | 1.7353 | 1.7416 | 1.6938 | 1.7726
Others
Δθint | Temperature rise due to surrounding heat sources |  | [°C] | 19.5102 | 20.4261 | 18.5416 | 18.5768 | 20.4279 | 19.4795
| Induced Voltage (standing) on Sheath |  | [V/km] | 205.0105 | 181.3251 | 238.4773 | 238.4773 | 181.3251 | 205.0105
| Induced Voltage angle on Sheath |  | [°] | -16.1096 | 95.432 | -166.2502 | -13.7498 | 84.568 | -163.8904
| Induced current on Metallic Screen |  | [A] | 0 | 0 | 0 | 0 | 0 | 0

## Cable - 1C...000MM2CU - FLAT-31
Cables Report
CYMCAP Version |  | 9.0 1 Revision
Study: |  | flat
Execution: |  | smoketest_multi_backfill_regression
Date: |  | 2026-01-01 00:00:00
No. | Description |  | Unit | 1
General Cable Information
1 | Cable Equipment ID |  |  | 1C132KV2000MM2CU
2 | Number of Cores |  |  | Single Core
3 | Voltage |  | [kV] | 132
4 | Conductor Area |  | [mm²] | 2000
5 | Cable Overall Diameter |  | [mm] | 137.6
6 | Maximum Steady-State Conductor Temperature |  | [°C] | 90
7 | Maximum Emergency Conductor Temperature |  | [°C] | 110
Conductor
8 | Material |  |  | Copper
9 | Electrical Resistivity at 20°C |  | [µΩ.cm] | 1.7241
10 | Temperature Coefficient at 20°C |  | [1/K] | 0.00393
11 | Reciprocal of Temperature Coefficient of Resistance (BETA) |  | [K] | 234.4529
12 | Volumetric Specific Heat (SH) |  | [J/(K*cm³)] | 3.45
13 | Construction |  |  | 6 Segments
14 | Conductor Insulation System |  |  | Extruded
15 | Milliken Wires Construction |  |  | Insulated Wires
16 | Ks (Skin Effect Coefficient) |  |  | 0.35
17 | Kp (Proximity Effect Coefficient) |  |  | 0.2
18 | Diameter |  | [mm] | 56.2
Conductor Shield
19 | Thickness |  | [mm] | 0.8
20 | Diameter |  | [mm] | 57.8
Insulation
21 | Material |  |  | XLPE Unfilled
22 | Thermal Resistivity |  | [K.m/W] | 3.5
23 | Dielectric Loss Factor - ( tan delta ) |  |  | 0.001
24 | Relative Permittivity - ( epsilon ) |  |  | 2.5
25 | Specific Insulation Resistance Constant at 60°F - ( K ) |  | [㏁.km] | 6096
26 | Thickness |  | [mm] | 18
27 | Diameter |  | [mm] | 93.8
Insulation Screen
28 | Material |  |  | Semi Conducting Screen
29 | Thickness |  | [mm] | 0.8
30 | Diameter |  | [mm] | 95.4
Non Metallic Layer - Water Barrier Tape
31 | Material |  |  | WATER SWELLABLE POLYMER
32 | Thermal Resistivity |  | [K.m/W] | 12
33 | Thickness |  | [mm] | 1.8
34 | Diameter |  | [mm] | 99
Sheath
35 | Is Sheath Around Each Core? |  |  | n/a
36 | Material |  |  | Aluminum
37 | Electrical Resistivity at 20°C |  | [µΩ.cm] | 2.84
38 | Temperature Coefficient at 20°C |  | [1/K] | 0.00403
39 | Reciprocal of Temperature Coefficient of Resistance (BETA) |  | [K] | 228
40 | Volumetric Specific Heat (SH) |  | [J/(K*cm³)] | 2.5
41 | Corrugation Type |  |  | Corrugated
42 | Thickness of the corrugated sheath |  | [mm] | 2.6
43 | Inner radius of the corrugated sheath |  | [mm] | 50
44 | Outer radius of the corrugated sheath |  | [mm] | 62
45 | Thickness |  | [mm] | 12
46 | Diameter |  | [mm] | 124
Jacket
47 | Material |  |  | Polyethylene
48 | Thermal Resistivity |  | [K.m/W] | 3.5
49 | Thickness |  | [mm] | 4
50 | Diameter |  | [mm] | 132
Non Metallic Layer - Nylon 12
51 | Material |  |  | POLYETHYLENE
52 | Thermal Resistivity |  | [K.m/W] | 3.5
53 | Thickness |  | [mm] | 0.8
54 | Diameter |  | [mm] | 133.6
Non Metallic Layer - Outer Jacket
55 | Material |  |  | POLYETHYLENE
56 | Thermal Resistivity |  | [K.m/W] | 3.5
57 | Thickness |  | [mm] | 2
58 | Diameter |  | [mm] | 137.6
No. | Description |  | Unit | 1
Specific Installation Data
59 | Cable Equipment ID |  |  | 1C132KV2000MM2CU
60 | Cable Frequency |  | [Hz] | 50
61 | Sheath / Shield Bonding |  |  | 1 Conductor 1 Point Bonded Flat
62 | Loss Factor Constant (ALOS) |  |  | 0.57
63 | Conduit construction |  |  | PVC Duct in Concrete
64 | Conduit material thermal resistivity |  | [K.m/W] | 6
65 | Conduit filling material |  |  | Air
66 | Inner diameter of the conduit |  | [mm] | 200
67 | Outer diameter of the conduit |  | [mm] | 225
Cable ID : 1C132KV2000MM2CU
Cable Title |  | 1c 132kV 2000mm2 Cu

## Impedances - FLAT-31
Cable Impedances & Admittances
CYMCAP Version |  | 9.0 1 Revision
Study: |  | flat
Execution: |  | smoketest_multi_backfill_regression
Date: |  | 2026-01-01 00:00:00
Earth Resistivity: [Ω.m] |  | 100
Frequency: [Hz] |  | 60
Temperature
|  |  | Circuit 1 | [5 empty] | Circuit 2
|  |  | Conductor |  |  | Sheath |  |  | Conductor |  |  | Sheath
|  | Phase | A | B | C | A | B | C | A | B | C | A | B | C
| Temperature | [°C] | 83.7916 | 88.1938 | 82.9165 | 72.0689 | 76.332 | 71.2212 | 82.8399 | 88.1987 | 83.885 | 71.147 | 76.3368 | 72.1592
R_Primitive [Ω/km]
|  |  | Circuit No. 1 |  |  | Circuit No. 2 |  |  | Circuit No. 1 |  |  | Circuit No. 2
|  |  | Conductor | [5 empty] | Sheath
|  | Phase | A | B | C | A | B | C | A | B | C | A | B | C
Circuit No. 1 | Conductor | A | 0.071345 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218
|  | B | 0.059218 | 0.07149 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218
|  | C | 0.059218 | 0.059218 | 0.07149 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218
Circuit No. 2 |  | A | 0.059218 | 0.059218 | 0.059218 | 0.07149 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218
|  | B | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.07149 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218
|  | C | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.07149 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218
Circuit No. 1 | Sheath | A | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.096776 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218
|  | B | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.097309 | 0.059218 | 0.059218 | 0.059218 | 0.059218
|  | C | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.097309 | 0.059218 | 0.059218 | 0.059218
Circuit No. 2 |  | A | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.097309 | 0.059218 | 0.059218
|  | B | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.097309 | 0.059218
|  | C | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.097309
X Primitive [Ω/km]
|  |  | Circuit No. 1 |  |  | Circuit No. 2 |  |  | Circuit No. 1 |  |  | Circuit No. 2
|  |  | Conductor | [5 empty] | Sheath
|  | Phase | A | B | C | A | B | C | A | B | C | A | B | C
Circuit No. 1 | Conductor | A | 0.79678 | 0.58779 | 0.53553 | 0.41418 | 0.42212 | 0.431 | 0.73177 | 0.58779 | 0.53553 | 0.41418 | 0.42212 | 0.431
|  | B | 0.58779 | 0.79678 | 0.58779 | 0.40699 | 0.41418 | 0.42212 | 0.58779 | 0.73177 | 0.58779 | 0.40699 | 0.41418 | 0.42212
|  | C | 0.53553 | 0.58779 | 0.79678 | 0.40043 | 0.40699 | 0.41418 | 0.53553 | 0.58779 | 0.73177 | 0.40043 | 0.40699 | 0.41418
Circuit No. 2 |  | A | 0.41418 | 0.40699 | 0.40043 | 0.79678 | 0.58779 | 0.53553 | 0.41418 | 0.40699 | 0.40043 | 0.73177 | 0.58779 | 0.53553
|  | B | 0.42212 | 0.41418 | 0.40699 | 0.58779 | 0.79678 | 0.58779 | 0.42212 | 0.41418 | 0.40699 | 0.58779 | 0.73177 | 0.58779
|  | C | 0.431 | 0.42212 | 0.41418 | 0.53553 | 0.58779 | 0.79678 | 0.431 | 0.42212 | 0.41418 | 0.53553 | 0.58779 | 0.73177
Circuit No. 1 | Sheath | A | 0.73177 | 0.58779 | 0.53553 | 0.41418 | 0.42212 | 0.431 | 0.73177 | 0.58779 | 0.53553 | 0.41418 | 0.42212 | 0.431
|  | B | 0.58779 | 0.73177 | 0.58779 | 0.40699 | 0.41418 | 0.42212 | 0.58779 | 0.73177 | 0.58779 | 0.40699 | 0.41418 | 0.42212
|  | C | 0.53553 | 0.58779 | 0.73177 | 0.40043 | 0.40699 | 0.41418 | 0.53553 | 0.58779 | 0.73177 | 0.40043 | 0.40699 | 0.41418
Circuit No. 2 |  | A | 0.41418 | 0.40699 | 0.40043 | 0.73177 | 0.58779 | 0.53553 | 0.41418 | 0.40699 | 0.40043 | 0.73177 | 0.58779 | 0.53553
|  | B | 0.42212 | 0.41418 | 0.40699 | 0.58779 | 0.73177 | 0.58779 | 0.42212 | 0.41418 | 0.40699 | 0.58779 | 0.73177 | 0.58779
|  | C | 0.431 | 0.42212 | 0.41418 | 0.53553 | 0.58779 | 0.73177 | 0.431 | 0.42212 | 0.41418 | 0.53553 | 0.58779 | 0.73177
R Bonding [Ω/km]
|  |  | Circuit No. 1 |  |  | Circuit No. 2
Conductor
|  | Phase | A | B | C | A | B | C
Circuit No. 1 | Conductor | A | 0.071345 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218
|  | B | 0.059218 | 0.07149 | 0.059218 | 0.059218 | 0.059218 | 0.059218
|  | C | 0.059218 | 0.059218 | 0.07149 | 0.059218 | 0.059218 | 0.059218
Circuit No. 2 |  | A | 0.059218 | 0.059218 | 0.059218 | 0.07149 | 0.059218 | 0.059218
|  | B | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.07149 | 0.059218
|  | C | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.07149
X Bonding [Ω/km]
|  |  | Circuit No. 1 |  |  | Circuit No. 2
Conductor
|  | Phase | A | B | C | A | B | C
Circuit No. 1 | Conductor | A | 0.79678 | 0.58779 | 0.53553 | 0.41418 | 0.42212 | 0.431
|  | B | 0.58779 | 0.79678 | 0.58779 | 0.40699 | 0.41418 | 0.42212
|  | C | 0.53553 | 0.58779 | 0.79678 | 0.40043 | 0.40699 | 0.41418
Circuit No. 2 |  | A | 0.41418 | 0.40699 | 0.40043 | 0.79678 | 0.58779 | 0.53553
|  | B | 0.42212 | 0.41418 | 0.40699 | 0.58779 | 0.79678 | 0.58779
|  | C | 0.431 | 0.42212 | 0.41418 | 0.53553 | 0.58779 | 0.79678
R Phase [Ω/km]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | A | B | C | A | B | C
Circuit No. 1 | A | 0.071345 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218
| B | 0.059218 | 0.07149 | 0.059218 | 0.059218 | 0.059218 | 0.059218
| C | 0.059218 | 0.059218 | 0.07149 | 0.059218 | 0.059218 | 0.059218
Circuit No. 2 | A | 0.059218 | 0.059218 | 0.059218 | 0.07149 | 0.059218 | 0.059218
| B | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.07149 | 0.059218
| C | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.07149
X Phase [Ω/km]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | A | B | C | A | B | C
Circuit No. 1 | A | 0.79678 | 0.58779 | 0.53553 | 0.41418 | 0.42212 | 0.431
| B | 0.58779 | 0.79678 | 0.58779 | 0.40699 | 0.41418 | 0.42212
| C | 0.53553 | 0.58779 | 0.79678 | 0.40043 | 0.40699 | 0.41418
Circuit No. 2 | A | 0.41418 | 0.40699 | 0.40043 | 0.79678 | 0.58779 | 0.53553
| B | 0.42212 | 0.41418 | 0.40699 | 0.58779 | 0.79678 | 0.58779
| C | 0.431 | 0.42212 | 0.41418 | 0.53553 | 0.58779 | 0.79678
R Circuit [Ω/km]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | A | B | C | A | B | C
Circuit No. 1 | A | 0.071345 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218
| B | 0.059218 | 0.07149 | 0.059218 | 0.059218 | 0.059218 | 0.059218
| C | 0.059218 | 0.059218 | 0.07149 | 0.059218 | 0.059218 | 0.059218
Circuit No. 2 | A | 0.059218 | 0.059218 | 0.059218 | 0.07149 | 0.059218 | 0.059218
| B | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.07149 | 0.059218
| C | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.07149
X Circuit [Ω/km]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | A | B | C | A | B | C
Circuit No. 1 | A | 0.79678 | 0.58779 | 0.53553 | 0.41418 | 0.42212 | 0.431
| B | 0.58779 | 0.79678 | 0.58779 | 0.40699 | 0.41418 | 0.42212
| C | 0.53553 | 0.58779 | 0.79678 | 0.40043 | 0.40699 | 0.41418
Circuit No. 2 | A | 0.41418 | 0.40699 | 0.40043 | 0.79678 | 0.58779 | 0.53553
| B | 0.42212 | 0.41418 | 0.40699 | 0.58779 | 0.79678 | 0.58779
| C | 0.431 | 0.42212 | 0.41418 | 0.53553 | 0.58779 | 0.79678
R Sequence [Ω/km]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | 0 | 1 | 2 | 0 | 1 | 2
Circuit No. 1 | 0 | 0.18988 | 0.015038 | -0.015135 | 0.17765 | -0.006931 | 0.006931
| 1 | -0.015135 | 0.012224 | -0.030222 | -0.006262 | -9e-05 | 0.00067
| 2 | 0.015038 | 0.030125 | 0.012224 | 0.006262 | -0.00067 | 9e-05
Circuit No. 2 | 0 | 0.17765 | 0.006262 | -0.006262 | 0.18993 | 0.015087 | -0.015087
| 1 | 0.006931 | 9e-05 | 0.00067 | -0.015087 | 0.012273 | -0.030174
| 2 | -0.006931 | -0.00067 | -9e-05 | 0.015087 | 0.030174 | 0.012273
X Sequence [Ω/km]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | 0 | 1 | 2 | 0 | 1 | 2
Circuit No. 1 | 0 | 1.9375 | -0.00871 | -0.00871 | 1.2441 | -0.011232 | -0.011232
| 1 | -0.00871 | 0.22642 | 0.017421 | 0.011619 | -0.000766 | -0.000387
| 2 | -0.00871 | 0.017421 | 0.22642 | 0.011619 | -0.000387 | -0.000766
Circuit No. 2 | 0 | 1.2441 | 0.011619 | 0.011619 | 1.9375 | -0.00871 | -0.00871
| 1 | -0.011232 | -0.000766 | -0.000387 | -0.00871 | 0.22642 | 0.017421
| 2 | -0.011232 | -0.000387 | -0.000766 | -0.00871 | 0.017421 | 0.22642
R Sequence/R1
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | 0 | 1 | 2 | 0 | 1 | 2
Circuit No. 1 | 0 | 15.4716 | 1.2254 | 1.2332 | 14.4756 | 0.56478 | 0.56478
| 1 | 1.2332 | 0.99606 | 2.4626 | 0.51021 | 0.007313 | 0.054574
| 2 | 1.2254 | 2.4547 | 0.99606 | 0.51021 | 0.054574 | 0.007313
Circuit No. 2 | 0 | 14.4756 | 0.51021 | 0.51021 | 15.4756 | 1.2293 | 1.2293
| 1 | 0.56478 | 0.007313 | 0.054574 | 1.2293 | 1 | 2.4586
| 2 | 0.56478 | 0.054574 | 0.007313 | 1.2293 | 2.4586 | 1
X Sequence/X1
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | 0 | 1 | 2 | 0 | 1 | 2
Circuit No. 1 | 0 | 8.5573 | 0.03847 | 0.03847 | 5.4945 | 0.049608 | 0.049608
| 1 | 0.03847 | 1 | 0.076941 | 0.051316 | 0.003381 | 0.001708
| 2 | 0.03847 | 0.076941 | 1 | 0.051316 | 0.001708 | 0.003381
Circuit No. 2 | 0 | 5.4945 | 0.051316 | 0.051316 | 8.5573 | 0.03847 | 0.03847
| 1 | 0.049608 | 0.003381 | 0.001708 | 0.03847 | 1 | 0.076941
| 2 | 0.049608 | 0.001708 | 0.003381 | 0.03847 | 0.076941 | 1
Symmetrical Components [Ω/km]
Circuit | Z0 | Circuit No. 1 0: Z1; Circuit No. 1 1: Z2; Circuit No. 1 2: ZOM(1,2)
1 | 0.189877 + j 1.937517 | Circuit No. 1 0: 0.012224 + j 0.226418; Circuit No. 1 1: 0.012224 + j 0.226418; Circuit No. 1 2: 0.177653 + j 1.24406
2 | 0.189925 + j 1.937517 | Circuit No. 1 0: 0.012273 + j 0.226418; Circuit No. 1 1: 0.012273 + j 0.226418; Circuit No. 1 2: 0.177653 + j 1.24406
Y Primitive [µS/km]
Circuit No. 1 |  | Circuit No. 1 1: Circuit No. 2
A | B | C | A | B | C
0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786
Y Circuit [µS/km]
Circuit No. 1 |  | Circuit No. 1 1: Circuit No. 2
A | B | C | A | B | C
0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786
Y Sequence [µS/km]
Circuit No. 1 |  | Circuit No. 1 1: Circuit No. 2
0 | 1 | 2 | 0 | 1 | 2
0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786

## Electrical...rameters - FLAT-31
Electrical Parameters
CYMCAP Version |  | 9.0 1 Revision
Study: |  | flat
Execution: |  | smoketest_multi_backfill_regression
Date: |  | 2026-01-01 00:00:00
No. | Description |  | Unit | Cable No.1 | Cable No.2 | Cable No.3 | Cable No.4 | Cable No.5 | Cable No.6
1 | Cable Equipment ID |  |  | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU
Resistances
2 | DC Resistance of the conductor at 20°C |  | [Ω/km] | 0.009 | 0.009 | 0.009 | 0.009 | 0.009 | 0.009
3 | DC Resistance of Conductor at Operating Temperature |  | [Ω/km] | 0.011256 | 0.011412 | 0.011225 | 0.011223 | 0.011412 | 0.01126
4 | AC Resistance of Conductor at 20°C |  | [Ω/km] | 0.010053 | 0.010053 | 0.010053 | 0.010053 | 0.010053 | 0.010053
5 | AC Resistance of Conductor at Operating Temperature |  | [Ω/km] | 0.012127 | 0.012273 | 0.012099 | 0.012096 | 0.012273 | 0.01213
6 | DC Resistance of Sheath at 20°C |  | [Ω/km] | 0.031044 | 0.031044 | 0.031044 | 0.031044 | 0.031044 | 0.031044
7 | DC Resistance of Sheath at Operating Temperature |  | [Ω/km] | 0.037558 | 0.038091 | 0.037452 | 0.037443 | 0.038092 | 0.037569
Losses
8 | Conductor Losses |  | [W/m] | 20.8118 | 21.0611 | 20.7623 | 20.758 | 21.0614 | 20.8171
9 | Dielectric Losses |  | [W/m] | 0.52341 | 0.52341 | 0.52341 | 0.52341 | 0.52341 | 0.52341
10 | Metallic Screen Losses |  | [W/m] | 1.0383 | 4.2188 | 1.1523 | 1.0391 | 4.2188 | 1.1514
11 | Armor/Pipe Losses |  | [W/m] | 0 | 0 | 0 | 0 | 0 | 0
12 | Total Losses |  | [W/m] | 22.3735 | 25.8033 | 22.438 | 22.3205 | 25.8036 | 22.4919
Capacitance, Inductance, Impedance
13 | Capacitance |  | [µF/km] | 0.287 | 0.287 | 0.287 | 0.287 | 0.287 | 0.287
14 | Inductance of Conductor |  | [mH/km] | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443 | 0.55443
15 | Reactance of Conductor |  | [Ω/km] | 0.17418 | 0.17418 | 0.17418 | 0.17418 | 0.17418 | 0.17418
16 | Inductance of Metallic Sheath |  | [mH/km] | 0.36652 | 0.36652 | 0.36652 | 0.36652 | 0.36652 | 0.36652
17 | Reactance of Metallic Sheath |  | [Ω/km] | 0.11514 | 0.11514 | 0.11514 | 0.11514 | 0.11514 | 0.11514
18 | Positive Sequence Impedance |  | [Ω/km] | 0.012127 + j0.174180 | 0.012273 + j0.174180 | 0.012099 + j0.174180 | 0.012096 + j0.174180 | 0.012273 + j0.174180 | 0.012130 + j0.174180
19 | Negative Sequence Impedance |  | [Ω/km] | 0.012127 + j0.174180 | 0.012273 + j0.174180 | 0.012099 + j0.174180 | 0.012096 + j0.174180 | 0.012273 + j0.174180 | 0.012130 + j0.174180
20 | Zero Sequence Impedance |  | [Ω/km] | 0.040717 + j0.059036 | 0.040700 + j0.059036 | 0.040720 + j0.059036 | 0.040721 + j0.059036 | 0.040700 + j0.059036 | 0.040716 + j0.059036
21 | Surge Impedance |  | [Ω] | 43.9635 | 43.9635 | 43.9635 | 43.9635 | 43.9635 | 43.9635
Complementary Information
22 | Dielectric Stress at Insulation Inner Surface |  | [kV/mm] | 5.4464 | 5.4464 | 5.4464 | 5.4464 | 5.4464 | 5.4464
23 | Dielectric Stress at Insulation Outer Surface |  | [kV/mm] | 3.3561 | 3.3561 | 3.3561 | 3.3561 | 3.3561 | 3.3561
24 | Insulation Resistance at 60°F (15.8°C) |  | [㏁.km] | 1281.8364 | 1281.8364 | 1281.8364 | 1281.8364 | 1281.8364 | 1281.8364
25 | Reduction Factor (2pt bonded & single metallic screen) |  |  | n/a | n/a | n/a | n/a | n/a | n/a
26 | Charging Current for One Cable (Phase) |  | [A/km] | 6.868 | 6.868 | 6.868 | 6.868 | 6.868 | 6.868
27 | Charging Capacity of three phase system at Uo |  | [kvar/km] | 1570.2251 | 1570.2251 | 1570.2251 | 1570.2251 | 1570.2251 | 1570.2251
28 | Voltage drop for Three Phase System |  | [V/A/km] | 0.021005 | 0.021257 | 0.020955 | 0.020951 | 0.021257 | 0.021011
29 | Induced Voltage (standing) on Sheath |  | [V/km] | 205.0105 | 181.3251 | 238.4773 | 238.4773 | 181.3251 | 205.0105
30 | Induced Voltage angle on Sheath |  | [°] | -16.1096 | 95.432 | -166.2502 | -13.7498 | 84.568 | -163.8904
31 | Induced current on Metallic Screen |  | [A] | 0 | 0 | 0 | 0 | 0 | 0

## Steady State - FLAT-31
Cable Parameters under Normal Operation
CYMCAP Version |  | 9.0 1 Revision
Study: |  | flat
Execution: |  | smoketest_multi_backfill_regression
Date: |  | 2026-01-01 00:00:00
No. | Symbol | Description | Unit | Cable No.1 | Cable No.2 | Cable No.3 | Cable No.4 | Cable No.5 | Cable No.6
1 |  | Cable Equipment ID |  | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU
Normal Operation IEC 60287-1-1
Conductor AC Resistance
2 | R₀ | DC Resistance of the conductor at 20°C | [Ω/km] | 0.009 | 0.009 | 0.009 | 0.009 | 0.009 | 0.009
3 | R' | DC Resistance of Conductor at Operating Temperature | [Ω/km] | 0.011256 | 0.011412 | 0.011225 | 0.011223 | 0.011412 | 0.01126
4 | dc | Conductor Diameter | [mm] | 56.2 | 56.2 | 56.2 | 56.2 | 56.2 | 56.2
5 | s | Distance Between Conductor Axes | [mm] | 350 | 350 | 350 | 350 | 350 | 350
6 | ks | Factor Used for xs Calculation (Skin Effect) |  | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
7 | kp | Factor Used for xp Calculation (Proximity Effect) |  | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
8 | Xs² | Factor Used for xp Calculation (Proximity Effect) |  | 3.9073 | 3.854 | 3.9181 | 3.9191 | 3.854 | 3.9062
9 | Xp² | Component of Yp Calculation (Proximity Effect) |  | 2.2328 | 2.2023 | 2.2389 | 2.2395 | 2.2023 | 2.2321
10 | ys | Skin Effect Factor |  | 0.074762 | 0.072854 | 0.07515 | 0.075184 | 0.072851 | 0.07472
11 | yp | Proximity Effect Factor |  | 0.0026247 | 0.0025609 | 0.0026377 | 0.0026389 | 0.0025608 | 0.0026234
12 | R | AC Resistance of Conductor at Operating Temperature | [Ω/km] | 0.012127 | 0.012273 | 0.012099 | 0.012096 | 0.012273 | 0.01213
Dielectric Losses
13 | tanδ | Dielectric Loss Factor |  | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001
14 | ε | Insulation Relative Permittivity |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
15 | C | Cable Capacitance | [µF/km] | 0.287 | 0.287 | 0.287 | 0.287 | 0.287 | 0.287
16 | U₀ | Voltage | [kV] | 76.2102 | 76.2102 | 76.2102 | 76.2102 | 76.2102 | 76.2102
17 | Wd | Cable Dielectric Losses Per Phase | [W/m] | 0.52341 | 0.52341 | 0.52341 | 0.52341 | 0.52341 | 0.52341
Circulating Loss Factor
18 | ƛ'sa | Circulating Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0
19 | ƛ'₁ | Screen Loss Factor Caused by Circulating Current |  | 0 | 0 | 0 | 0 | 0 | 0
Eddy Loss Factor
20 | Rs | AC Resistance used for Eddy Loss Factor computation | [Ω/km] | 0.037558 | 0.038091 | 0.037452 | 0.037443 | 0.038092 | 0.037569
21 | d | Mean diameter used for Eddy Loss Factor computation | [mm] | 112 | 112 | 112 | 112 | 112 | 112
22 | ρs | Electrical Resistivity used for Eddy Loss Factor computation | [Ω.m] | 3.4359e-08 | 3.4847e-08 | 3.4262e-08 | 3.4254e-08 | 3.4848e-08 | 3.437e-08
23 | Ds | External diameter used for Eddy Loss Factor computation | [mm] | 124 | 124 | 124 | 124 | 124 | 124
24 | ts | Thickness used for Eddy Loss Factor computation | [mm] | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
25 | β₁ | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 107.1907 | 106.4376 | 107.3424 | 107.3557 | 106.4368 | 107.1746
26 | gs | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 1.014 | 1.0139 | 1.0141 | 1.0141 | 1.0139 | 1.014
27 | m | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 0.83646 | 0.82475 | 0.83883 | 0.83904 | 0.82474 | 0.83621
28 | ƛ₀ | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 0.015807 | 0.062183 | 0.01586 | 0.015865 | 0.062182 | 0.015802
29 | Δ₁ | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | -0.028988 | 0.015874 | 0.083194 | -0.028887 | 0.015874 | 0.083076
30 | Δ₂ | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 0.0026264 | 0 | 0.00011529 | 0.0026439 | 0 | 0.00011492
31 | F | Milliken conductor Effect |  | 1 | 1 | 1 | 1 | 1 | 1
32 | Fpipe | Magnetic effect factor due to pipe |  | 1 | 1 | 1 | 1 | 1 | 1
33 | Farmour | Magnetic effect factor due to armour |  | 1 | 1 | 1 | 1 | 1 | 1
34 | ƛ''₁ | Screen Loss Factor Caused by Eddy Current |  | 0.049891 | 0.20031 | 0.055499 | 0.050058 | 0.20031 | 0.055311
Metallic Screen Loss factor
35 | ƛ₁ | Screen Loss Factor |  | 0.049891 | 0.20031 | 0.055499 | 0.050058 | 0.20031 | 0.055311
Armour and Pipe Loss Factor
36 | ƛ₂a | Armour Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0
37 | ƛ₂pipe | Pipe Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0
38 | ƛ₂ | Armour Loss Factor + Pipe Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0
Normal Operation IEC 60287-2-1
39 | T₁ | Thermal Resistance Between Conductor and Screen | [K.m/W] | 0.55629 | 0.55629 | 0.55629 | 0.55629 | 0.55629 | 0.55629
40 | t₁ | Insulation Thickness Between Conductor and Screen | [mm] | 19.6 | 19.6 | 19.6 | 19.6 | 19.6 | 19.6
41 | ρTi | Thermal Resistivity of Insulation | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
42 | T₃ | Thermal Resistance of Jacket/Pipe Coating | [K.m/W] | 0.10188 | 0.10188 | 0.10188 | 0.10188 | 0.10188 | 0.10188
43 | t₃ | Thickness of Jacket/Pipe Coating | [mm] | 4 | 4 | 4 | 4 | 4 | 4
44 | ρTJ | Thermal Resistivity of Jacket/Pipe Coating | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
45 | T Conductor Shield | Thermal resistance | [K.m/W] | 0.015637 | 0.015637 | 0.015637 | 0.015637 | 0.015637 | 0.015637
46 |  | Thermal resistance equation
47 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
48 |  | Layer thickness | [mm] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
49 |  | Internal diameter | [mm] | 56.2 | 56.2 | 56.2 | 56.2 | 56.2 | 56.2
50 | T Insulation | Thermal resistance | [K.m/W] | 0.26971 | 0.26971 | 0.26971 | 0.26971 | 0.26971 | 0.26971
51 |  | Thermal resistance equation
52 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
53 |  | Layer thickness | [mm] | 18 | 18 | 18 | 18 | 18 | 18
54 |  | Internal diameter | [mm] | 57.8 | 57.8 | 57.8 | 57.8 | 57.8 | 57.8
55 | T Insulation Screen | Thermal resistance | [K.m/W] | 0.0094217 | 0.0094217 | 0.0094217 | 0.0094217 | 0.0094217 | 0.0094217
56 |  | Thermal resistance equation
57 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
58 |  | Layer thickness | [mm] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
59 |  | Internal diameter | [mm] | 93.8 | 93.8 | 93.8 | 93.8 | 93.8 | 93.8
60 | T Water Barrier Tape | Thermal resistance | [K.m/W] | 0.26152 | 0.26152 | 0.26152 | 0.26152 | 0.26152 | 0.26152
61 |  | Thermal resistance equation
62 |  | Thermal resistivity | [K.m/W] | 12 | 12 | 12 | 12 | 12 | 12
63 |  | Layer thickness | [mm] | 7 | 7 | 7 | 7 | 7 | 7
64 |  | Internal diameter | [mm] | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4
65 | T Sheath | Thermal resistance | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
66 |  | Thermal resistance equation
67 |  | Thermal resistivity | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
68 |  | Layer thickness | [mm] | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5
69 |  | Internal diameter | [mm] | 99 | 99 | 99 | 99 | 99 | 99
70 | T Jacket | Thermal resistance | [K.m/W] | 0.07874 | 0.07874 | 0.07874 | 0.07874 | 0.07874 | 0.07874
71 |  | Thermal resistance equation
72 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
73 |  | Layer thickness | [mm] | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7
74 |  | Internal diameter | [mm] | 114.6 | 114.6 | 114.6 | 114.6 | 114.6 | 114.6
75 | T Nylon 12 | Thermal resistance | [K.m/W] | 0.0067114 | 0.0067114 | 0.0067114 | 0.0067114 | 0.0067114 | 0.0067114
76 |  | Thermal resistance equation
77 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
78 |  | Layer thickness | [mm] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
79 |  | Internal diameter | [mm] | 132 | 132 | 132 | 132 | 132 | 132
80 | T Outer Jacket | Thermal resistance | [K.m/W] | 0.016433 | 0.016433 | 0.016433 | 0.016433 | 0.016433 | 0.016433
81 |  | Thermal resistance equation
82 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
83 |  | Layer thickness | [mm] | 2 | 2 | 2 | 2 | 2 | 2
84 |  | Internal diameter | [mm] | 133.6 | 133.6 | 133.6 | 133.6 | 133.6 | 133.6
Thermal resistance inside the duct
85 | U | Constant from IEC6028721 clause4272 |  | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87
86 | V | Constant from IEC6028721 clause4272 |  | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312
87 | Y | Constant from IEC6028721 clause4272 |  | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037
88 | θm | Mean temperature of the medium in conduit | [°C] | 67.3915 | 70.9946 | 66.518 | 66.4678 | 70.9994 | 67.458
89 | Deq | Equivalent diameter of the cables inside the conduit | [mm] | 137.6 | 137.6 | 137.6 | 137.6 | 137.6 | 137.6
90 | T₄' | Thermal resistance of the medium in conduit | [K.m/W] | 0.21435 | 0.20993 | 0.21545 | 0.21551 | 0.20993 | 0.21426
Thermal resistance of the duct
91 | Do | Outer diameter of the conduit | [mm] | 225 | 225 | 225 | 225 | 225 | 225
92 | Di | Inner diameter of the conduit | [mm] | 200 | 200 | 200 | 200 | 200 | 200
93 | ρT | Thermal resistivity of the conduit material | [K.m/W] | 6 | 6 | 6 | 6 | 6 | 6
94 | T₄'' | Thermal resistance of the conduit | [K.m/W] | 0.11247 | 0.11247 | 0.11247 | 0.11247 | 0.11247 | 0.11247
Thermal resistance of the external medium
95 | L | Depth of cable/conduit axis | [m] | 1.1588 | 1.1588 | 1.1588 | 1.1588 | 1.1588 | 1.1588
96 | De / Do | External diameter of the cable conduit | [m] | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225
97 | u | Geometric factor as per IEC60287-2-1 clause 4.2.2 |  | 10.3004 | 10.3004 | 10.3004 | 10.3004 | 10.3004 | 10.3004
98 | ρTs | Thermal resistivity of the soil | [K.m/W] | 1.2048 | 1.2047 | 1.2076 | 1.2084 | 1.2049 | 1.2051
99 | T₄'''self | Thermal resistance of the cable isolated | [K.m/W] | 0.57964 | 0.57959 | 0.58102 | 0.58138 | 0.5797 | 0.57979
100 | T₄'''mutual | Thermal resistance associated to the temperature rise due to surrounding heat sources | [K.m/W] | 0.87202 | 0.79161 | 0.82635 | 0.83228 | 0.79167 | 0.86607
101 | Δθint | Temperature rise due to surrounding heat sources | [°C] | 19.5102 | 20.4261 | 18.5416 | 18.5768 | 20.4279 | 19.4795
102 | T₄''' | Thermal resistance of the external medium | [K.m/W] | 1.4517 | 1.3712 | 1.4074 | 1.4137 | 1.3714 | 1.4459
Thermal Capacitance IEC 853-2
103 | Q Conductor | Thermal capacitance | [J/m.K]
104 |  | Thermal capacitance equation
105 |  | Material surface | [mm²] | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
106 |  | Volumetric specific heat of the material | [J/(K*m³)] | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000
107 | Q Conductor Shield | Thermal capacitance | [J/m.K]
108 |  | Thermal capacitance equation
109 |  | External diameter | [mm] | 57.8 | 57.8 | 57.8 | 57.8 | 57.8 | 57.8
110 |  | Internal diameter | [mm] | 56.2 | 56.2 | 56.2 | 56.2 | 56.2 | 56.2
111 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
112 | Q1 Insulation | Thermal capacitance | [J/m.K]
113 |  | Thermal capacitance equation
114 |  | External diameter | [mm] | 93.8 | 93.8 | 93.8 | 93.8 | 93.8 | 93.8
115 |  | Internal diameter | [mm] | 57.8 | 57.8 | 57.8 | 57.8 | 57.8 | 57.8
116 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
117 | Q2 Insulation | Thermal capacitance | [J/m.K]
118 |  | Thermal capacitance equation
119 |  | External diameter | [mm] | 93.8 | 93.8 | 93.8 | 93.8 | 93.8 | 93.8
120 |  | Internal diameter | [mm] | 57.8 | 57.8 | 57.8 | 57.8 | 57.8 | 57.8
121 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
122 | Q Insulation Screen | Thermal capacitance | [J/m.K]
123 |  | Thermal capacitance equation
124 |  | External diameter | [mm] | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4
125 |  | Internal diameter | [mm] | 93.8 | 93.8 | 93.8 | 93.8 | 93.8 | 93.8
126 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
127 | Q Water Barrier Tape | Thermal capacitance | [J/m.K]
128 |  | Thermal capacitance equation
129 |  | External diameter | [mm] | 99 | 99 | 99 | 99 | 99 | 99
130 |  | Internal diameter | [mm] | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4
131 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
132 | Q Sheath | Thermal capacitance | [J/m.K]
133 |  | Thermal capacitance equation
134 |  | Material surface | [mm²] | 914.8318 | 914.8318 | 914.8318 | 914.8318 | 914.8318 | 914.8318
135 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
136 | Q Jacket | Thermal capacitance | [J/m.K]
137 |  | Thermal capacitance equation
138 |  | External diameter | [mm] | 132 | 132 | 132 | 132 | 132 | 132
139 |  | Internal diameter | [mm] | 124 | 124 | 124 | 124 | 124 | 124
140 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
141 | Q Nylon 12 | Thermal capacitance | [J/m.K]
142 |  | Thermal capacitance equation
143 |  | External diameter | [mm] | 133.6 | 133.6 | 133.6 | 133.6 | 133.6 | 133.6
144 |  | Internal diameter | [mm] | 132 | 132 | 132 | 132 | 132 | 132
145 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
146 | Q Outer Jacket | Thermal capacitance | [J/m.K]
147 |  | Thermal capacitance equation
148 |  | External diameter | [mm] | 137.6 | 137.6 | 137.6 | 137.6 | 137.6 | 137.6
149 |  | Internal diameter | [mm] | 133.6 | 133.6 | 133.6 | 133.6 | 133.6 | 133.6
150 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
Ampacity
151 | T₄ | Total external thermal resistance | [K.m/W] | 1.7785 | 1.6936 | 1.7353 | 1.7416 | 1.6938 | 1.7726
152 | I | Cable core ampacity | [A] | 1310 | 1310 | 1310 | 1310 | 1310 | 1310

## Short Circ...- 1C132KV2000MM2CU
Cable Short Circuit
CYMCAP Version |  | 9.0 1 Revision
Cable Title |  | 1c 132kV 2000mm2 Cu
Date: |  | smoketest_multi_backfill_regression
2026-01-01 00:00:00
Symbol | Description |  | Unit | Circuit No. 1
| Cable Equipment ID |  |  | 1C132KV2000MM2CU
|  |  |  | Conductor |  |  | Sheath
|  |  |  | A | B | C | A | B | C
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483 | 147.7945 | 147.7945 | 147.7945
S | Layer Cross-Sectional Area |  | [mm²] | 2000 | 2000 | 2000 | 991.6123 | 991.6123 | 991.6123
θi | Initial Temperature |  | [°C] | 83.7869 | 88.1991 | 82.9129 | 72.0637 | 76.3386 | 71.2174
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529 | 228.139 | 228.139 | 228.139
θf | Final Temperature |  | [°C] | 250 | 250 | 250 | 150 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 925119.4831 | 909836.4061 | 928141.6667 | 222649.5297 | 215721.7934 | 224007.1661
Inad | Non Adiabatic Short Circuit Current |  | [A] | 926475.3168 | 911169.8413 | 929501.9296 | 225591.5753 | 218572.2974 | 226967.1512
Symbol | Description |  | Unit | Circuit No. 2
| Cable Equipment ID |  |  | 1C132KV2000MM2CU
|  |  |  | Conductor |  |  | Sheath
|  |  |  | A | B | C | A | B | C
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483 | 147.7945 | 147.7945 | 147.7945
S | Layer Cross-Sectional Area |  | [mm²] | 2000 | 2000 | 2000 | 991.6123 | 991.6123 | 991.6123
θi | Initial Temperature |  | [°C] | 82.836 | 88.204 | 83.8805 | 71.1428 | 76.3433 | 72.1545
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529 | 228.139 | 228.139 | 228.139
θf | Final Temperature |  | [°C] | 250 | 250 | 250 | 150 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 928407.4817 | 909819.475 | 924795.6019 | 224126.4896 | 215714.0642 | 222503.7125
Inad | Non Adiabatic Short Circuit Current |  | [A] | 929768.1342 | 911152.8854 | 926150.961 | 227088.0515 | 218564.466 | 225443.8313