## General Su...ry Report - FLAT-9
General Summary Report
CYMCAP Version |  | 9.0 1 Revision
Study: |  | flat
Execution: |  | smoketest_single_backfill
Date: |  | 2026-01-01 00:00:00
Simulation Data
Installation type: |  | Multiple Ductbanks
Steady State Option |  | Temperature
Ambient temperature [°C] |  | 32
Native Soil Thermal Resistivity [K.m/W] |  | 1.36
Consider Non-Isothermal Earth Surface |  | No
Consider effect of soil dry out |  | No
Consider Electrical interaction between circuits |  | No
Induced current in metallic layers as a fraction of conductor current (applied to all single phase circuits) [A] |  | 0
Installation Type:Multiple Ductbanks/Backfills
Ambient Soil Temperature at Installation Depth [°C] |  | 32
Native Soil Thermal Resistivity [K.m/W] |  | 1.36
Consider Non-Isothermal Earth Surface |  | No
Layer Name |  | X [m] | Y [m] | Width [m] | Height [m] | Thermal Resistivity [K.m/W]
Backfill |  | 0 | 1 | 2.5 | 0.8 | 1
General Cable Information
Cable ID |  | Number of Cores | Conductor Construction | Voltage [kV] | Conductor Area [mm²] | Cable Overall Diameter [mm] | Maximum Steady-State Conductor Temperature [ºC] | Maximum Emergency Conductor Temperature [ºC]
1C132KV2000MM2CU |  | Single Core | 6 Segments | 132 | 2000 | 137.6 | 90 | 110
Detailed Cable Information
Cable ID |  | Conductor | Insulation | Sheath / Tape | Concentric Wires | Filler | Armour | Jacket / Armour Serving
1C132KV2000MM2CU |  | Copper | XLPE Unfilled | Aluminum | n/a | n/a | n/a | Polyethylene
General Input Data
Cable | Cable ID | Circuit No. | Phase | Fq [Hz] | X [m] | Y [m] | DLF [p.u.] | Sheath / Shield Bonding
Cable Index Number | Cable Equipment ID | Circuit No. | Cable Phase | Operating Frequency | X coordinate | Y coordinate | Daily Load Factor | Bonding Type
1 | 1C132KV2000MM2CU | 1 | A | 50 | -1 | 1.1588 | 0.57 | 1 Conductor 1 Point Bonded Flat
2 | 1C132KV2000MM2CU | 1 | B | 50 | -0.6 | 1.1588 | 0.57 | 1 Conductor 1 Point Bonded Flat
3 | 1C132KV2000MM2CU | 1 | C | 50 | -0.2 | 1.1588 | 0.57 | 1 Conductor 1 Point Bonded Flat
4 | 1C132KV2000MM2CU | 2 | A | 50 | 0.2 | 1.1588 | 0.57 | 1 Conductor 1 Point Bonded Flat
5 | 1C132KV2000MM2CU | 2 | B | 50 | 0.6 | 1.1588 | 0.57 | 1 Conductor 1 Point Bonded Flat
6 | 1C132KV2000MM2CU | 2 | C | 50 | 1 | 1.1588 | 0.57 | 1 Conductor 1 Point Bonded Flat
Ampacity and Temperatures
Cable | Cable ID | I [A] | θc [°C] | θs [°C] | θa [°C] | θsurf [°C] | θduct [°C] | θair / θcasing [°C]
Cable Index Number | Cable Equipment ID | Steady State Ampacity | Conductor temperature | Sheath/Shield temperature | Armour temperature | Cable surface temperature | Duct surface temperature | Mean air temperature in the tunnel / Casing surface temperature
1 | 1C132KV2000MM2CU | 1500 | 82.9383 | 67.6574 | n/a | 64.7238 | 55.095 | n/a
2 | 1C132KV2000MM2CU | 1500 | 88.4167 | 72.9092 | n/a | 69.6103 | 58.9763 | n/a
3 | 1C132KV2000MM2CU | 1500 | 88.3116 | 72.8089 | n/a | 69.8264 | 60.2326 | n/a
4 | 1C132KV2000MM2CU | 1500 | 88.2628 | 72.7621 | n/a | 69.7887 | 60.2235 | n/a
5 | 1C132KV2000MM2CU | 1500 | 88.4173 | 72.9098 | n/a | 69.6109 | 58.9769 | n/a
6 | 1C132KV2000MM2CU | 1500 | 82.9855 | 67.7026 | n/a | 64.7599 | 55.102 | n/a
Electrical Resistances
Cable | Cable ID | R₀ [Ω/km] | ys | yp | R [Ω/km] | R's [Ω/km] | R'w [Ω/km] | R'a [Ω/km]
Cable Index Number | Cable Equipment ID | DC Resistance of the conductor at 20°C | Skin Effect Factor | Proximity Effect Factor | AC Resistance of Conductor at Operating Temperature | DC Resistance of Sheath at Operating Temperature | DC Resistance of Concentric Wires at Operating Temperature | DC Resistance of Armor at Operating Temperature
1 | 1C132KV2000MM2CU | 0.009 | 0.07514 | 0.0020183 | 0.012092 | 0.037006 | n/a | n/a
2 | 1C132KV2000MM2CU | 0.009 | 0.072759 | 0.0019573 | 0.012273 | 0.037663 | n/a | n/a
3 | 1C132KV2000MM2CU | 0.009 | 0.072803 | 0.0019584 | 0.01227 | 0.037651 | n/a | n/a
4 | 1C132KV2000MM2CU | 0.009 | 0.072824 | 0.001959 | 0.012268 | 0.037645 | n/a | n/a
5 | 1C132KV2000MM2CU | 0.009 | 0.072759 | 0.0019573 | 0.012273 | 0.037663 | n/a | n/a
6 | 1C132KV2000MM2CU | 0.009 | 0.075119 | 0.0020178 | 0.012094 | 0.037012 | n/a | n/a
Thermal Resistances
Cable | Cable ID | T₁ [K.m/W] | T₂ [K.m/W] | T₃ [K.m/W] | T₄' [K.m/W] | T₄'' [K.m/W] | T₄''' [K.m/W] | T₄ [K.m/W]
Cable Index Number | Cable Equipment ID | Thermal resistance of insulation | Thermal resistance of bedding | Thermal resistance of outer covering | Thermal resistance inside the duct | Thermal resistance of the duct | Thermal resistance of the external medium | Total external thermal resistance
1 | 1C132KV2000MM2CU | 0.55629 | 0 | 0.10188 | 0.22194 | 0.11247 | 0.80215 | 1.1366
2 | 1C132KV2000MM2CU | 0.55629 | 0 | 0.10188 | 0.21596 | 0.11247 | 0.83313 | 1.1616
3 | 1C132KV2000MM2CU | 0.55629 | 0 | 0.10188 | 0.21525 | 0.11247 | 0.96442 | 1.2921
4 | 1C132KV2000MM2CU | 0.55629 | 0 | 0.10188 | 0.21528 | 0.11247 | 0.96708 | 1.2948
5 | 1C132KV2000MM2CU | 0.55629 | 0 | 0.10188 | 0.21596 | 0.11247 | 0.83315 | 1.1616
6 | 1C132KV2000MM2CU | 0.55629 | 0 | 0.10188 | 0.22191 | 0.11247 | 0.79989 | 1.1343
Losses
Cable | Cable ID | Wc [W/m] | Wd [W/m] | Ws [W/m] | Wa [W/m] | Wt [W/m] | ƛ₁ | ƛ₂
Cable Index Number | Cable Equipment ID | Conductor Losses | Dielectric Losses | Metallic Screen Losses | Armor/Pipe Losses | Total Losses | Screen Loss Factor | Armour Loss Factor + Pipe Loss Factor
1 | 1C132KV2000MM2CU | 27.2077 | 0.52341 | 1.0617 | 0 | 28.7928 | 0.039022 | 0
2 | 1C132KV2000MM2CU | 27.6146 | 0.52341 | 4.2404 | 0 | 32.3784 | 0.15356 | 0
3 | 1C132KV2000MM2CU | 27.6068 | 0.52341 | 1.1438 | 0 | 29.2739 | 0.04143 | 0
4 | 1C132KV2000MM2CU | 27.6031 | 0.52341 | 1.0573 | 0 | 29.1839 | 0.038304 | 0
5 | 1C132KV2000MM2CU | 27.6146 | 0.52341 | 4.2404 | 0 | 32.3785 | 0.15356 | 0
6 | 1C132KV2000MM2CU | 27.2112 | 0.52341 | 1.1483 | 0 | 28.883 | 0.042201 | 0
Complementary Information
Cable | Cable ID | Δθint [°C] | [A] | [µF/km] | [Ω] | [Ω/km] | [Ω/km] | [V/A/km]
Cable Index Number | Cable Equipment ID | Temperature rise due to surrounding heat sources | Induced current on Metallic Screen | Cable Capacitance | Surge Impedance | Reactance of Conductor | Reactance of Metallic Sheath | Voltage drop for Three Phase System
1 | 1C132KV2000MM2CU | 15.0474 | 0 | 0.287 | 45.0099 | 0.18257 | 0.12353 | 0.020945
2 | 1C132KV2000MM2CU | 18.0553 | 0 | 0.287 | 45.0099 | 0.18257 | 0.12353 | 0.021258
3 | 1C132KV2000MM2CU | 20.1835 | 0 | 0.287 | 45.0099 | 0.18257 | 0.12353 | 0.021252
4 | 1C132KV2000MM2CU | 20.2002 | 0 | 0.287 | 45.0099 | 0.18257 | 0.12353 | 0.021249
5 | 1C132KV2000MM2CU | 18.0556 | 0 | 0.287 | 45.0099 | 0.18257 | 0.12353 | 0.021258
6 | 1C132KV2000MM2CU | 15.0339 | 0 | 0.287 | 45.0099 | 0.18257 | 0.12353 | 0.020947

## Study Summary - FLAT-9
Study Summary
CYMCAP Version |  | 9.0 1 Revision
Study: |  | flat
Execution: |  | smoketest_single_backfill
Date: |  | 2026-01-01 00:00:00
General Simulation Data
Steady State Option | [8 empty] | Temperature
Consider Electrical interaction between circuits | [8 empty] | No
Induced currents in metallic layers as a fraction of conductor current (applied to all single phase circuits) : | [8 empty] | 0
Conductor Resistances Computation Option: | [8 empty] | IEC-228
Standard Settings Options
General guidance | [8 empty] | Custom
Factor on RAC due to magnetic armour | [8 empty] | CIGREGuidance
Factor on RAC due to magnetic duct | [8 empty] | CIGREGuidance
Factor on ƛ₁ due to magnetic armour | [8 empty] | CYMCAPGuidance
Factor on ƛ₁ due to magnetic duct | [8 empty] | CIGREGuidance
Factor on ƛ₂ due to ƛ'₁ | [8 empty] | CYMCAPGuidance
ƛ''₁ computation | [8 empty] | CIGREGuidance
ƛ₂pipe computation | [8 empty] | CYMCAPGuidance
Wd computation | [8 empty] | CIGREGuidance
T₂ computation | [8 empty] | CIGREGuidance
T₄ computation | [8 empty] | CYMCAPGuidance
Installation Type:Multiple Ductbanks/Backfills
Ambient Soil Temperature at Installation Depth [°C] | [8 empty] | 32
Native Soil Thermal Resistivity [K.m/W] | [8 empty] | 1.36
Consider Non-Isothermal Earth Surface | [8 empty] | No
Layer Name |  | X [m] | Y [m] | Width [m] | Height [m] | Thermal Resistivity [K.m/W]
Backfill |  | 0 | 1 | 2.5 | 0.8 | 1
Results Summary
Cable No. | Cable ID | Circuit No. | Cable Phase | Cable Frequency | Daily Load Factor | X coordinate [m] | Y coordinate [m] | Conductor temperature [°C] | Ampacity [A]
1 | 1C132KV2000MM2CU | 1 | A | 50 | 0.57 | -1 | 1.1588 | 82.9383 | 1500
2 | 1C132KV2000MM2CU | 1 | B | 50 | 0.57 | -0.6 | 1.1588 | 88.4167 | 1500
3 | 1C132KV2000MM2CU | 1 | C | 50 | 0.57 | -0.2 | 1.1588 | 88.3116 | 1500
4 | 1C132KV2000MM2CU | 2 | A | 50 | 0.57 | 0.2 | 1.1588 | 88.2628 | 1500
5 | 1C132KV2000MM2CU | 2 | B | 50 | 0.57 | 0.6 | 1.1588 | 88.4173 | 1500
6 | 1C132KV2000MM2CU | 2 | C | 50 | 0.57 | 1 | 1.1588 | 82.9855 | 1500

## Steady State Summary - FLAT-9
Steady State Summary
CYMCAP Version |  | 9.0 1 Revision
Study: |  | flat
Execution: |  | smoketest_single_backfill
Date: |  | 2026-01-01 00:00:00
Simulation Data
Installation type: |  | Multiple Ductbanks
Steady State Option |  | Temperature
Ambient temperature [°C] |  | 32
Native Soil Thermal Resistivity [K.m/W] |  | 1.36
Consider Non-Isothermal Earth Surface |  | No
Consider effect of soil dry out |  | No
Consider Electrical interaction between circuits |  | No
Induced current in metallic layers as a fraction of conductor current (applied to all single phase circuits) [A] |  | 0
Variable | Description |  | Unit | Cables
Cable No. | Cable Index Number |  |  | 1 | 2 | 3 | 4 | 5 | 6
General Input Data
Cable ID | Cable Equipment ID |  |  | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU
Circuit No. | Circuit No. |  |  | 1 | 1 | 1 | 2 | 2 | 2
Phase | Cable Phase |  |  | A | B | C | A | B | C
Fq | Operating Frequency |  | [Hz] | 50 | 50 | 50 | 50 | 50 | 50
X | X coordinate |  | [m] | -1 | -0.6 | -0.2 | 0.2 | 0.6 | 1
Y | Y coordinate |  | [m] | 1.1588 | 1.1588 | 1.1588 | 1.1588 | 1.1588 | 1.1588
DLF | Daily Load Factor |  | [p.u.] | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57
| Bonding Type |  |  | 1 Conductor 1 Point Bonded Flat | 1 Conductor 1 Point Bonded Flat | 1 Conductor 1 Point Bonded Flat | 1 Conductor 1 Point Bonded Flat | 1 Conductor 1 Point Bonded Flat | 1 Conductor 1 Point Bonded Flat
Ampacity
I | Steady State Ampacity |  | [A] | 1500 | 1500 | 1500 | 1500 | 1500 | 1500
I₀ | Steady State Ampacity without insulation temperature drop constraint |  | [A] | n/a | n/a | n/a | n/a | n/a | n/a
Temperatures
θc | Conductor temperature |  | [°C] | 82.9383 | 88.4167 | 88.3116 | 88.2628 | 88.4173 | 82.9855
Δθins | Temperature drop across the insulation |  | [°C] | n/a | n/a | n/a | n/a | n/a | n/a
θs | Sheath/Shield temperature |  | [°C] | 67.6574 | 72.9092 | 72.8089 | 72.7621 | 72.9098 | 67.7026
θa | Armour temperature |  | [°C] | n/a | n/a | n/a | n/a | n/a | n/a
θsurf | Cable surface temperature |  | [°C] | 64.7238 | 69.6103 | 69.8264 | 69.7887 | 69.6109 | 64.7599
θduct | Duct surface temperature |  | [°C] | 55.095 | 58.9763 | 60.2326 | 60.2235 | 58.9769 | 55.102
Resistances
R₀ | DC Resistance of the conductor at 20°C |  | [Ω/km] | 0.009 | 0.009 | 0.009 | 0.009 | 0.009 | 0.009
R | AC Resistance of the Conductor at Operating Temperature |  | [Ω/km] | 0.012092 | 0.012273 | 0.01227 | 0.012268 | 0.012273 | 0.012094
ys | Skin Effect Factor |  |  | 0.07514 | 0.072759 | 0.072803 | 0.072824 | 0.072759 | 0.075119
yp | Proximity Effect Factor |  |  | 0.0020183 | 0.0019573 | 0.0019584 | 0.001959 | 0.0019573 | 0.0020178
Losses
Wc | Conductor Losses |  | [W/m] | 27.2077 | 27.6146 | 27.6068 | 27.6031 | 27.6146 | 27.2112
Wd | Dielectric Losses |  | [W/m] | 0.52341 | 0.52341 | 0.52341 | 0.52341 | 0.52341 | 0.52341
Ws | Metallic Screen Losses |  | [W/m] | 1.0617 | 4.2404 | 1.1438 | 1.0573 | 4.2404 | 1.1483
Wa | Armor/Pipe Losses |  | [W/m] | 0 | 0 | 0 | 0 | 0 | 0
Wt | Total Losses |  | [W/m] | 28.7928 | 32.3784 | 29.2739 | 29.1839 | 32.3785 | 28.883
ƛ₁ | Screen Loss Factor |  |  | 0.039022 | 0.15356 | 0.04143 | 0.038304 | 0.15356 | 0.042201
ƛ₂ | Armour Loss Factor + Pipe Loss Factor |  |  | 0 | 0 | 0 | 0 | 0 | 0
Thermal resistances
T1 | Thermal Resistance Between Conductor and Screen |  | [K.m/W] | 0.55629 | 0.55629 | 0.55629 | 0.55629 | 0.55629 | 0.55629
T2 | Thermal Resistance Between Screen and Armour |  | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
T3 | Thermal Resistance of the Jacket/Pipe Coating |  | [K.m/W] | 0.10188 | 0.10188 | 0.10188 | 0.10188 | 0.10188 | 0.10188
T4 | Total external thermal resistance |  | [K.m/W] | 1.1366 | 1.1616 | 1.2921 | 1.2948 | 1.1616 | 1.1343
Others
Δθint | Temperature rise due to surrounding heat sources |  | [°C] | 15.0474 | 18.0553 | 20.1835 | 20.2002 | 18.0556 | 15.0339
| Induced Voltage (standing) on Sheath |  | [V/km] | 319.5738 | 226.1334 | 176.5051 | 176.5051 | 226.1334 | 319.5737
| Induced Voltage angle on Sheath |  | [°] | -13.6902 | 72.529 | -150 | -30 | 107.471 | -166.3098
| Induced current on Metallic Screen |  | [A] | 0 | 0 | 0 | 0 | 0 | 0

## Cable - 1C...2000MM2CU - FLAT-9
Cables Report
CYMCAP Version |  | 9.0 1 Revision
Study: |  | flat
Execution: |  | smoketest_single_backfill
Date: |  | 2026-01-01 00:00:00
No. | Description |  | Unit | 1
General Cable Information
1 | Cable Equipment ID |  |  | 1C132KV2000MM2CU
2 | Number of Cores |  |  | Single Core
3 | Voltage |  | [kV] | 132
4 | Conductor Area |  | [mm²] | 2000
5 | Cable Overall Diameter |  | [mm] | 137.6
6 | Maximum Steady-State Conductor Temperature |  | [°C] | 90
7 | Maximum Emergency Conductor Temperature |  | [°C] | 110
Conductor
8 | Material |  |  | Copper
9 | Electrical Resistivity at 20°C |  | [µΩ.cm] | 1.7241
10 | Temperature Coefficient at 20°C |  | [1/K] | 0.00393
11 | Reciprocal of Temperature Coefficient of Resistance (BETA) |  | [K] | 234.4529
12 | Volumetric Specific Heat (SH) |  | [J/(K*cm³)] | 3.45
13 | Construction |  |  | 6 Segments
14 | Conductor Insulation System |  |  | Extruded
15 | Milliken Wires Construction |  |  | Insulated Wires
16 | Ks (Skin Effect Coefficient) |  |  | 0.35
17 | Kp (Proximity Effect Coefficient) |  |  | 0.2
18 | Diameter |  | [mm] | 56.2
Conductor Shield
19 | Thickness |  | [mm] | 0.8
20 | Diameter |  | [mm] | 57.8
Insulation
21 | Material |  |  | XLPE Unfilled
22 | Thermal Resistivity |  | [K.m/W] | 3.5
23 | Dielectric Loss Factor - ( tan delta ) |  |  | 0.001
24 | Relative Permittivity - ( epsilon ) |  |  | 2.5
25 | Specific Insulation Resistance Constant at 60°F - ( K ) |  | [㏁.km] | 6096
26 | Thickness |  | [mm] | 18
27 | Diameter |  | [mm] | 93.8
Insulation Screen
28 | Material |  |  | Semi Conducting Screen
29 | Thickness |  | [mm] | 0.8
30 | Diameter |  | [mm] | 95.4
Non Metallic Layer - Water Barrier Tape
31 | Material |  |  | WATER SWELLABLE POLYMER
32 | Thermal Resistivity |  | [K.m/W] | 12
33 | Thickness |  | [mm] | 1.8
34 | Diameter |  | [mm] | 99
Sheath
35 | Is Sheath Around Each Core? |  |  | n/a
36 | Material |  |  | Aluminum
37 | Electrical Resistivity at 20°C |  | [µΩ.cm] | 2.84
38 | Temperature Coefficient at 20°C |  | [1/K] | 0.00403
39 | Reciprocal of Temperature Coefficient of Resistance (BETA) |  | [K] | 228
40 | Volumetric Specific Heat (SH) |  | [J/(K*cm³)] | 2.5
41 | Corrugation Type |  |  | Corrugated
42 | Thickness of the corrugated sheath |  | [mm] | 2.6
43 | Inner radius of the corrugated sheath |  | [mm] | 50
44 | Outer radius of the corrugated sheath |  | [mm] | 62
45 | Thickness |  | [mm] | 12
46 | Diameter |  | [mm] | 124
Jacket
47 | Material |  |  | Polyethylene
48 | Thermal Resistivity |  | [K.m/W] | 3.5
49 | Thickness |  | [mm] | 4
50 | Diameter |  | [mm] | 132
Non Metallic Layer - Nylon 12
51 | Material |  |  | POLYETHYLENE
52 | Thermal Resistivity |  | [K.m/W] | 3.5
53 | Thickness |  | [mm] | 0.8
54 | Diameter |  | [mm] | 133.6
Non Metallic Layer - Outer Jacket
55 | Material |  |  | POLYETHYLENE
56 | Thermal Resistivity |  | [K.m/W] | 3.5
57 | Thickness |  | [mm] | 2
58 | Diameter |  | [mm] | 137.6
No. | Description |  | Unit | 1
Specific Installation Data
59 | Cable Equipment ID |  |  | 1C132KV2000MM2CU
60 | Cable Frequency |  | [Hz] | 50
61 | Sheath / Shield Bonding |  |  | 1 Conductor 1 Point Bonded Flat
62 | Loss Factor Constant (ALOS) |  |  | 0.57
63 | Conduit construction |  |  | PVC Duct in Concrete
64 | Conduit material thermal resistivity |  | [K.m/W] | 6
65 | Conduit filling material |  |  | Air
66 | Inner diameter of the conduit |  | [mm] | 200
67 | Outer diameter of the conduit |  | [mm] | 225
Cable ID : 1C132KV2000MM2CU
Cable Title |  | 1c 132kV 2000mm2 Cu

## Impedances - FLAT-9
Cable Impedances & Admittances
CYMCAP Version |  | 9.0 1 Revision
Study: |  | flat
Execution: |  | smoketest_single_backfill
Date: |  | 2026-01-01 00:00:00
Earth Resistivity: [Ω.m] |  | 100
Frequency: [Hz] |  | 60
Temperature
|  |  | Circuit 1 | [5 empty] | Circuit 2
|  |  | Conductor |  |  | Sheath |  |  | Conductor |  |  | Sheath
|  | Phase | A | B | C | A | B | C | A | B | C | A | B | C
| Temperature | [°C] | 82.9383 | 88.4167 | 88.3116 | 67.6574 | 72.9092 | 72.8089 | 88.2628 | 88.4173 | 82.9855 | 72.7621 | 72.9098 | 67.7026
R_Primitive [Ω/km]
|  |  | Circuit No. 1 |  |  | Circuit No. 2 |  |  | Circuit No. 1 |  |  | Circuit No. 2
|  |  | Conductor | [5 empty] | Sheath
|  | Phase | A | B | C | A | B | C | A | B | C | A | B | C
Circuit No. 1 | Conductor | A | 0.07131 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218
|  | B | 0.059218 | 0.071491 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218
|  | C | 0.059218 | 0.059218 | 0.071491 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218
Circuit No. 2 |  | A | 0.059218 | 0.059218 | 0.059218 | 0.071491 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218
|  | B | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.071491 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218
|  | C | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.071491 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218
Circuit No. 1 | Sheath | A | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.096224 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218
|  | B | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.096881 | 0.059218 | 0.059218 | 0.059218 | 0.059218
|  | C | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.096881 | 0.059218 | 0.059218 | 0.059218
Circuit No. 2 |  | A | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.096881 | 0.059218 | 0.059218
|  | B | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.096881 | 0.059218
|  | C | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.096881
X Primitive [Ω/km]
|  |  | Circuit No. 1 |  |  | Circuit No. 2 |  |  | Circuit No. 1 |  |  | Circuit No. 2
|  |  | Conductor | [5 empty] | Sheath
|  | Phase | A | B | C | A | B | C | A | B | C | A | B | C
Circuit No. 1 | Conductor | A | 0.79678 | 0.57772 | 0.52546 | 0.49489 | 0.47319 | 0.45637 | 0.73177 | 0.57772 | 0.52546 | 0.49489 | 0.47319 | 0.45637
|  | B | 0.57772 | 0.79678 | 0.57772 | 0.52546 | 0.49489 | 0.47319 | 0.57772 | 0.73177 | 0.57772 | 0.52546 | 0.49489 | 0.47319
|  | C | 0.52546 | 0.57772 | 0.79678 | 0.57772 | 0.52546 | 0.49489 | 0.52546 | 0.57772 | 0.73177 | 0.57772 | 0.52546 | 0.49489
Circuit No. 2 |  | A | 0.49489 | 0.52546 | 0.57772 | 0.79678 | 0.57772 | 0.52546 | 0.49489 | 0.52546 | 0.57772 | 0.73177 | 0.57772 | 0.52546
|  | B | 0.47319 | 0.49489 | 0.52546 | 0.57772 | 0.79678 | 0.57772 | 0.47319 | 0.49489 | 0.52546 | 0.57772 | 0.73177 | 0.57772
|  | C | 0.45637 | 0.47319 | 0.49489 | 0.52546 | 0.57772 | 0.79678 | 0.45637 | 0.47319 | 0.49489 | 0.52546 | 0.57772 | 0.73177
Circuit No. 1 | Sheath | A | 0.73177 | 0.57772 | 0.52546 | 0.49489 | 0.47319 | 0.45637 | 0.73177 | 0.57772 | 0.52546 | 0.49489 | 0.47319 | 0.45637
|  | B | 0.57772 | 0.73177 | 0.57772 | 0.52546 | 0.49489 | 0.47319 | 0.57772 | 0.73177 | 0.57772 | 0.52546 | 0.49489 | 0.47319
|  | C | 0.52546 | 0.57772 | 0.73177 | 0.57772 | 0.52546 | 0.49489 | 0.52546 | 0.57772 | 0.73177 | 0.57772 | 0.52546 | 0.49489
Circuit No. 2 |  | A | 0.49489 | 0.52546 | 0.57772 | 0.73177 | 0.57772 | 0.52546 | 0.49489 | 0.52546 | 0.57772 | 0.73177 | 0.57772 | 0.52546
|  | B | 0.47319 | 0.49489 | 0.52546 | 0.57772 | 0.73177 | 0.57772 | 0.47319 | 0.49489 | 0.52546 | 0.57772 | 0.73177 | 0.57772
|  | C | 0.45637 | 0.47319 | 0.49489 | 0.52546 | 0.57772 | 0.73177 | 0.45637 | 0.47319 | 0.49489 | 0.52546 | 0.57772 | 0.73177
R Bonding [Ω/km]
|  |  | Circuit No. 1 |  |  | Circuit No. 2
Conductor
|  | Phase | A | B | C | A | B | C
Circuit No. 1 | Conductor | A | 0.07131 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218
|  | B | 0.059218 | 0.071491 | 0.059218 | 0.059218 | 0.059218 | 0.059218
|  | C | 0.059218 | 0.059218 | 0.071491 | 0.059218 | 0.059218 | 0.059218
Circuit No. 2 |  | A | 0.059218 | 0.059218 | 0.059218 | 0.071491 | 0.059218 | 0.059218
|  | B | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.071491 | 0.059218
|  | C | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.071491
X Bonding [Ω/km]
|  |  | Circuit No. 1 |  |  | Circuit No. 2
Conductor
|  | Phase | A | B | C | A | B | C
Circuit No. 1 | Conductor | A | 0.79678 | 0.57772 | 0.52546 | 0.49489 | 0.47319 | 0.45637
|  | B | 0.57772 | 0.79678 | 0.57772 | 0.52546 | 0.49489 | 0.47319
|  | C | 0.52546 | 0.57772 | 0.79678 | 0.57772 | 0.52546 | 0.49489
Circuit No. 2 |  | A | 0.49489 | 0.52546 | 0.57772 | 0.79678 | 0.57772 | 0.52546
|  | B | 0.47319 | 0.49489 | 0.52546 | 0.57772 | 0.79678 | 0.57772
|  | C | 0.45637 | 0.47319 | 0.49489 | 0.52546 | 0.57772 | 0.79678
R Phase [Ω/km]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | A | B | C | A | B | C
Circuit No. 1 | A | 0.07131 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218
| B | 0.059218 | 0.071491 | 0.059218 | 0.059218 | 0.059218 | 0.059218
| C | 0.059218 | 0.059218 | 0.071491 | 0.059218 | 0.059218 | 0.059218
Circuit No. 2 | A | 0.059218 | 0.059218 | 0.059218 | 0.071491 | 0.059218 | 0.059218
| B | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.071491 | 0.059218
| C | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.071491
X Phase [Ω/km]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | A | B | C | A | B | C
Circuit No. 1 | A | 0.79678 | 0.57772 | 0.52546 | 0.49489 | 0.47319 | 0.45637
| B | 0.57772 | 0.79678 | 0.57772 | 0.52546 | 0.49489 | 0.47319
| C | 0.52546 | 0.57772 | 0.79678 | 0.57772 | 0.52546 | 0.49489
Circuit No. 2 | A | 0.49489 | 0.52546 | 0.57772 | 0.79678 | 0.57772 | 0.52546
| B | 0.47319 | 0.49489 | 0.52546 | 0.57772 | 0.79678 | 0.57772
| C | 0.45637 | 0.47319 | 0.49489 | 0.52546 | 0.57772 | 0.79678
R Circuit [Ω/km]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | A | B | C | A | B | C
Circuit No. 1 | A | 0.07131 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218
| B | 0.059218 | 0.071491 | 0.059218 | 0.059218 | 0.059218 | 0.059218
| C | 0.059218 | 0.059218 | 0.071491 | 0.059218 | 0.059218 | 0.059218
Circuit No. 2 | A | 0.059218 | 0.059218 | 0.059218 | 0.071491 | 0.059218 | 0.059218
| B | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.071491 | 0.059218
| C | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.059218 | 0.071491
X Circuit [Ω/km]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | A | B | C | A | B | C
Circuit No. 1 | A | 0.79678 | 0.57772 | 0.52546 | 0.49489 | 0.47319 | 0.45637
| B | 0.57772 | 0.79678 | 0.57772 | 0.52546 | 0.49489 | 0.47319
| C | 0.52546 | 0.57772 | 0.79678 | 0.57772 | 0.52546 | 0.49489
Circuit No. 2 | A | 0.49489 | 0.52546 | 0.57772 | 0.79678 | 0.57772 | 0.52546
| B | 0.47319 | 0.49489 | 0.52546 | 0.57772 | 0.79678 | 0.57772
| C | 0.45637 | 0.47319 | 0.49489 | 0.52546 | 0.57772 | 0.79678
R Sequence [Ω/km]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | 0 | 1 | 2 | 0 | 1 | 2
Circuit No. 1 | 0 | 0.18987 | 0.015026 | -0.015147 | 0.17765 | 0.019944 | -0.019944
| 1 | -0.015147 | 0.012213 | -0.030234 | 0.030174 | 0.004857 | 0.01023
| 2 | 0.015026 | 0.030113 | 0.012213 | -0.030174 | -0.01023 | -0.004857
Circuit No. 2 | 0 | 0.17765 | -0.030174 | 0.030174 | 0.18993 | 0.015087 | -0.015087
| 1 | -0.019944 | -0.004857 | 0.01023 | -0.015087 | 0.012273 | -0.030174
| 2 | 0.019944 | -0.01023 | 0.004857 | 0.015087 | 0.030174 | 0.012273
X Sequence [Ω/km]
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | 0 | 1 | 2 | 0 | 1 | 2
Circuit No. 1 | 0 | 1.9174 | -0.00871 | -0.00871 | 1.5054 | 0.046356 | 0.046356
| 1 | -0.00871 | 0.23649 | 0.017421 | -0.04045 | -0.010347 | -0.005906
| 2 | -0.00871 | 0.017421 | 0.23649 | -0.04045 | -0.005906 | -0.010347
Circuit No. 2 | 0 | 1.5054 | -0.04045 | -0.04045 | 1.9174 | -0.00871 | -0.00871
| 1 | 0.046356 | -0.010347 | -0.005906 | -0.00871 | 0.23649 | 0.017421
| 2 | 0.046356 | -0.005906 | -0.010347 | -0.00871 | 0.017421 | 0.23649
R Sequence/R1
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | 0 | 1 | 2 | 0 | 1 | 2
Circuit No. 1 | 0 | 15.4701 | 1.2243 | 1.2342 | 14.475 | 1.625 | 1.625
| 1 | 1.2342 | 0.99509 | 2.4634 | 2.4585 | 0.39573 | 0.83352
| 2 | 1.2243 | 2.4536 | 0.99509 | 2.4585 | 0.83352 | 0.39573
Circuit No. 2 | 0 | 14.475 | 2.4585 | 2.4585 | 15.475 | 1.2293 | 1.2293
| 1 | 1.625 | 0.39573 | 0.83352 | 1.2293 | 1 | 2.4585
| 2 | 1.625 | 0.83352 | 0.39573 | 1.2293 | 2.4585 | 1
X Sequence/X1
|  | Circuit No. 1 |  |  | Circuit No. 2
|  | 0 | 1 | 2 | 0 | 1 | 2
Circuit No. 1 | 0 | 8.1078 | 0.036832 | 0.036832 | 6.3655 | 0.19602 | 0.19602
| 1 | 0.036832 | 1 | 0.073665 | 0.17105 | 0.043751 | 0.024975
| 2 | 0.036832 | 0.073665 | 1 | 0.17105 | 0.024975 | 0.043751
Circuit No. 2 | 0 | 6.3655 | 0.17105 | 0.17105 | 8.1078 | 0.036832 | 0.036832
| 1 | 0.19602 | 0.043751 | 0.024975 | 0.036832 | 1 | 0.073665
| 2 | 0.19602 | 0.024975 | 0.043751 | 0.036832 | 0.073665 | 1
Symmetrical Components [Ω/km]
Circuit | Z0 | Circuit No. 1 0: Z1; Circuit No. 1 1: Z2; Circuit No. 1 2: ZOM(1,2)
1 | 0.189866 + j 1.917381 | Circuit No. 1 0: 0.012213 + j 0.236486; Circuit No. 1 1: 0.012213 + j 0.236486; Circuit No. 1 2: 0.177653 + j 1.505351
2 | 0.189926 + j 1.917381 | Circuit No. 1 0: 0.012273 + j 0.236486; Circuit No. 1 1: 0.012273 + j 0.236486; Circuit No. 1 2: 0.177653 + j 1.505351
Y Primitive [µS/km]
Circuit No. 1 |  | Circuit No. 1 1: Circuit No. 2
A | B | C | A | B | C
0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786
Y Circuit [µS/km]
Circuit No. 1 |  | Circuit No. 1 1: Circuit No. 2
A | B | C | A | B | C
0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786
Y Sequence [µS/km]
Circuit No. 1 |  | Circuit No. 1 1: Circuit No. 2
0 | 1 | 2 | 0 | 1 | 2
0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786 | 0.108241 + j 108.240786

## Electrical Parameters - FLAT-9
Electrical Parameters
CYMCAP Version |  | 9.0 1 Revision
Study: |  | flat
Execution: |  | smoketest_single_backfill
Date: |  | 2026-01-01 00:00:00
No. | Description |  | Unit | Cable No.1 | Cable No.2 | Cable No.3 | Cable No.4 | Cable No.5 | Cable No.6
1 | Cable Equipment ID |  |  | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU
Resistances
2 | DC Resistance of the conductor at 20°C |  | [Ω/km] | 0.009 | 0.009 | 0.009 | 0.009 | 0.009 | 0.009
3 | DC Resistance of Conductor at Operating Temperature |  | [Ω/km] | 0.011226 | 0.01142 | 0.011416 | 0.011414 | 0.01142 | 0.011228
4 | AC Resistance of Conductor at 20°C |  | [Ω/km] | 0.010045 | 0.010045 | 0.010045 | 0.010045 | 0.010045 | 0.010045
5 | AC Resistance of Conductor at Operating Temperature |  | [Ω/km] | 0.012092 | 0.012273 | 0.01227 | 0.012268 | 0.012273 | 0.012094
6 | DC Resistance of Sheath at 20°C |  | [Ω/km] | 0.031044 | 0.031044 | 0.031044 | 0.031044 | 0.031044 | 0.031044
7 | DC Resistance of Sheath at Operating Temperature |  | [Ω/km] | 0.037006 | 0.037663 | 0.037651 | 0.037645 | 0.037663 | 0.037012
Losses
8 | Conductor Losses |  | [W/m] | 27.2077 | 27.6146 | 27.6068 | 27.6031 | 27.6146 | 27.2112
9 | Dielectric Losses |  | [W/m] | 0.52341 | 0.52341 | 0.52341 | 0.52341 | 0.52341 | 0.52341
10 | Metallic Screen Losses |  | [W/m] | 1.0617 | 4.2404 | 1.1438 | 1.0573 | 4.2404 | 1.1483
11 | Armor/Pipe Losses |  | [W/m] | 0 | 0 | 0 | 0 | 0 | 0
12 | Total Losses |  | [W/m] | 28.7928 | 32.3784 | 29.2739 | 29.1839 | 32.3785 | 28.883
Capacitance, Inductance, Impedance
13 | Capacitance |  | [µF/km] | 0.287 | 0.287 | 0.287 | 0.287 | 0.287 | 0.287
14 | Inductance of Conductor |  | [mH/km] | 0.58114 | 0.58114 | 0.58114 | 0.58114 | 0.58114 | 0.58114
15 | Reactance of Conductor |  | [Ω/km] | 0.18257 | 0.18257 | 0.18257 | 0.18257 | 0.18257 | 0.18257
16 | Inductance of Metallic Sheath |  | [mH/km] | 0.39322 | 0.39322 | 0.39322 | 0.39322 | 0.39322 | 0.39322
17 | Reactance of Metallic Sheath |  | [Ω/km] | 0.12353 | 0.12353 | 0.12353 | 0.12353 | 0.12353 | 0.12353
18 | Positive Sequence Impedance |  | [Ω/km] | 0.012092 + j0.182570 | 0.012273 + j0.182570 | 0.012270 + j0.182570 | 0.012268 + j0.182570 | 0.012273 + j0.182570 | 0.012094 + j0.182570
19 | Negative Sequence Impedance |  | [Ω/km] | 0.012092 + j0.182570 | 0.012273 + j0.182570 | 0.012270 + j0.182570 | 0.012268 + j0.182570 | 0.012273 + j0.182570 | 0.012094 + j0.182570
20 | Zero Sequence Impedance |  | [Ω/km] | 0.040720 + j0.059036 | 0.040699 + j0.059036 | 0.040699 + j0.059036 | 0.040699 + j0.059036 | 0.040699 + j0.059036 | 0.040720 + j0.059036
21 | Surge Impedance |  | [Ω] | 45.0099 | 45.0099 | 45.0099 | 45.0099 | 45.0099 | 45.0099
Complementary Information
22 | Dielectric Stress at Insulation Inner Surface |  | [kV/mm] | 5.4464 | 5.4464 | 5.4464 | 5.4464 | 5.4464 | 5.4464
23 | Dielectric Stress at Insulation Outer Surface |  | [kV/mm] | 3.3561 | 3.3561 | 3.3561 | 3.3561 | 3.3561 | 3.3561
24 | Insulation Resistance at 60°F (15.8°C) |  | [㏁.km] | 1281.8364 | 1281.8364 | 1281.8364 | 1281.8364 | 1281.8364 | 1281.8364
25 | Reduction Factor (2pt bonded & single metallic screen) |  |  | n/a | n/a | n/a | n/a | n/a | n/a
26 | Charging Current for One Cable (Phase) |  | [A/km] | 6.868 | 6.868 | 6.868 | 6.868 | 6.868 | 6.868
27 | Charging Capacity of three phase system at Uo |  | [kvar/km] | 1570.2251 | 1570.2251 | 1570.2251 | 1570.2251 | 1570.2251 | 1570.2251
28 | Voltage drop for Three Phase System |  | [V/A/km] | 0.020945 | 0.021258 | 0.021252 | 0.021249 | 0.021258 | 0.020947
29 | Induced Voltage (standing) on Sheath |  | [V/km] | 319.5738 | 226.1334 | 176.5051 | 176.5051 | 226.1334 | 319.5737
30 | Induced Voltage angle on Sheath |  | [°] | -13.6902 | 72.529 | -150 | -30 | 107.471 | -166.3098
31 | Induced current on Metallic Screen |  | [A] | 0 | 0 | 0 | 0 | 0 | 0

## Steady State - FLAT-9
Cable Parameters under Normal Operation
CYMCAP Version |  | 9.0 1 Revision
Study: |  | flat
Execution: |  | smoketest_single_backfill
Date: |  | 2026-01-01 00:00:00
No. | Symbol | Description | Unit | Cable No.1 | Cable No.2 | Cable No.3 | Cable No.4 | Cable No.5 | Cable No.6
1 |  | Cable Equipment ID |  | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU | 1C132KV2000MM2CU
Normal Operation IEC 60287-1-1
Conductor AC Resistance
2 | R₀ | DC Resistance of the conductor at 20°C | [Ω/km] | 0.009 | 0.009 | 0.009 | 0.009 | 0.009 | 0.009
3 | R' | DC Resistance of Conductor at Operating Temperature | [Ω/km] | 0.011226 | 0.01142 | 0.011416 | 0.011414 | 0.01142 | 0.011228
4 | dc | Conductor Diameter | [mm] | 56.2 | 56.2 | 56.2 | 56.2 | 56.2 | 56.2
5 | s | Distance Between Conductor Axes | [mm] | 400 | 400 | 400 | 400 | 400 | 400
6 | ks | Factor Used for xs Calculation (Skin Effect) |  | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
7 | kp | Factor Used for xp Calculation (Proximity Effect) |  | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
8 | Xs² | Factor Used for xp Calculation (Proximity Effect) |  | 3.9179 | 3.8514 | 3.8526 | 3.8532 | 3.8514 | 3.9173
9 | Xp² | Component of Yp Calculation (Proximity Effect) |  | 2.2388 | 2.2008 | 2.2015 | 2.2018 | 2.2008 | 2.2384
10 | ys | Skin Effect Factor |  | 0.07514 | 0.072759 | 0.072803 | 0.072824 | 0.072759 | 0.075119
11 | yp | Proximity Effect Factor |  | 0.0020183 | 0.0019573 | 0.0019584 | 0.001959 | 0.0019573 | 0.0020178
12 | R | AC Resistance of Conductor at Operating Temperature | [Ω/km] | 0.012092 | 0.012273 | 0.01227 | 0.012268 | 0.012273 | 0.012094
Dielectric Losses
13 | tanδ | Dielectric Loss Factor |  | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001
14 | ε | Insulation Relative Permittivity |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
15 | C | Cable Capacitance | [µF/km] | 0.287 | 0.287 | 0.287 | 0.287 | 0.287 | 0.287
16 | U₀ | Voltage | [kV] | 76.2102 | 76.2102 | 76.2102 | 76.2102 | 76.2102 | 76.2102
17 | Wd | Cable Dielectric Losses Per Phase | [W/m] | 0.52341 | 0.52341 | 0.52341 | 0.52341 | 0.52341 | 0.52341
Circulating Loss Factor
18 | ƛ'sa | Circulating Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0
19 | ƛ'₁ | Screen Loss Factor Caused by Circulating Current |  | 0 | 0 | 0 | 0 | 0 | 0
Eddy Loss Factor
20 | Rs | AC Resistance used for Eddy Loss Factor computation | [Ω/km] | 0.037006 | 0.037663 | 0.037651 | 0.037645 | 0.037663 | 0.037012
21 | d | Mean diameter used for Eddy Loss Factor computation | [mm] | 112 | 112 | 112 | 112 | 112 | 112
22 | ρs | Electrical Resistivity used for Eddy Loss Factor computation | [Ω.m] | 3.3854e-08 | 3.4456e-08 | 3.4444e-08 | 3.4439e-08 | 3.4456e-08 | 3.386e-08
23 | Ds | External diameter used for Eddy Loss Factor computation | [mm] | 124 | 124 | 124 | 124 | 124 | 124
24 | ts | Thickness used for Eddy Loss Factor computation | [mm] | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
25 | β₁ | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 107.9871 | 107.041 | 107.0588 | 107.0672 | 107.0409 | 107.9788
26 | gs | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 1.0142 | 1.014 | 1.014 | 1.014 | 1.014 | 1.0142
27 | m | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 0.84894 | 0.83413 | 0.8344 | 0.83453 | 0.83412 | 0.84881
28 | ƛ₀ | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 0.012314 | 0.048251 | 0.012067 | 0.01207 | 0.048251 | 0.012312
29 | Δ₁ | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | -0.022265 | 0.012504 | 0.06242 | -0.022749 | 0.012504 | 0.062886
30 | Δ₂ | Coefficient used in IEC 60287-1-1 Clause 2.3.6.1 |  | 0.0018535 | 0 | 4.9526e-05 | 0.0017898 | 0 | 5.0267e-05
31 | F | Milliken conductor Effect |  | 1 | 1 | 1 | 1 | 1 | 1
32 | Fpipe | Magnetic effect factor due to pipe |  | 1 | 1 | 1 | 1 | 1 | 1
33 | Farmour | Magnetic effect factor due to armour |  | 1 | 1 | 1 | 1 | 1 | 1
34 | ƛ''₁ | Screen Loss Factor Caused by Eddy Current |  | 0.039022 | 0.15356 | 0.04143 | 0.038304 | 0.15356 | 0.042201
Metallic Screen Loss factor
35 | ƛ₁ | Screen Loss Factor |  | 0.039022 | 0.15356 | 0.04143 | 0.038304 | 0.15356 | 0.042201
Armour and Pipe Loss Factor
36 | ƛ₂a | Armour Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0
37 | ƛ₂pipe | Pipe Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0
38 | ƛ₂ | Armour Loss Factor + Pipe Loss Factor |  | 0 | 0 | 0 | 0 | 0 | 0
Normal Operation IEC 60287-2-1
39 | T₁ | Thermal Resistance Between Conductor and Screen | [K.m/W] | 0.55629 | 0.55629 | 0.55629 | 0.55629 | 0.55629 | 0.55629
40 | t₁ | Insulation Thickness Between Conductor and Screen | [mm] | 19.6 | 19.6 | 19.6 | 19.6 | 19.6 | 19.6
41 | ρTi | Thermal Resistivity of Insulation | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
42 | T₃ | Thermal Resistance of Jacket/Pipe Coating | [K.m/W] | 0.10188 | 0.10188 | 0.10188 | 0.10188 | 0.10188 | 0.10188
43 | t₃ | Thickness of Jacket/Pipe Coating | [mm] | 4 | 4 | 4 | 4 | 4 | 4
44 | ρTJ | Thermal Resistivity of Jacket/Pipe Coating | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
45 | T Conductor Shield | Thermal resistance | [K.m/W] | 0.015637 | 0.015637 | 0.015637 | 0.015637 | 0.015637 | 0.015637
46 |  | Thermal resistance equation
47 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
48 |  | Layer thickness | [mm] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
49 |  | Internal diameter | [mm] | 56.2 | 56.2 | 56.2 | 56.2 | 56.2 | 56.2
50 | T Insulation | Thermal resistance | [K.m/W] | 0.26971 | 0.26971 | 0.26971 | 0.26971 | 0.26971 | 0.26971
51 |  | Thermal resistance equation
52 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
53 |  | Layer thickness | [mm] | 18 | 18 | 18 | 18 | 18 | 18
54 |  | Internal diameter | [mm] | 57.8 | 57.8 | 57.8 | 57.8 | 57.8 | 57.8
55 | T Insulation Screen | Thermal resistance | [K.m/W] | 0.0094217 | 0.0094217 | 0.0094217 | 0.0094217 | 0.0094217 | 0.0094217
56 |  | Thermal resistance equation
57 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
58 |  | Layer thickness | [mm] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
59 |  | Internal diameter | [mm] | 93.8 | 93.8 | 93.8 | 93.8 | 93.8 | 93.8
60 | T Water Barrier Tape | Thermal resistance | [K.m/W] | 0.26152 | 0.26152 | 0.26152 | 0.26152 | 0.26152 | 0.26152
61 |  | Thermal resistance equation
62 |  | Thermal resistivity | [K.m/W] | 12 | 12 | 12 | 12 | 12 | 12
63 |  | Layer thickness | [mm] | 7 | 7 | 7 | 7 | 7 | 7
64 |  | Internal diameter | [mm] | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4
65 | T Sheath | Thermal resistance | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
66 |  | Thermal resistance equation
67 |  | Thermal resistivity | [K.m/W] | 0 | 0 | 0 | 0 | 0 | 0
68 |  | Layer thickness | [mm] | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5
69 |  | Internal diameter | [mm] | 99 | 99 | 99 | 99 | 99 | 99
70 | T Jacket | Thermal resistance | [K.m/W] | 0.07874 | 0.07874 | 0.07874 | 0.07874 | 0.07874 | 0.07874
71 |  | Thermal resistance equation
72 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
73 |  | Layer thickness | [mm] | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7
74 |  | Internal diameter | [mm] | 114.6 | 114.6 | 114.6 | 114.6 | 114.6 | 114.6
75 | T Nylon 12 | Thermal resistance | [K.m/W] | 0.0067114 | 0.0067114 | 0.0067114 | 0.0067114 | 0.0067114 | 0.0067114
76 |  | Thermal resistance equation
77 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
78 |  | Layer thickness | [mm] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
79 |  | Internal diameter | [mm] | 132 | 132 | 132 | 132 | 132 | 132
80 | T Outer Jacket | Thermal resistance | [K.m/W] | 0.016433 | 0.016433 | 0.016433 | 0.016433 | 0.016433 | 0.016433
81 |  | Thermal resistance equation
82 |  | Thermal resistivity | [K.m/W] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
83 |  | Layer thickness | [mm] | 2 | 2 | 2 | 2 | 2 | 2
84 |  | Internal diameter | [mm] | 133.6 | 133.6 | 133.6 | 133.6 | 133.6 | 133.6
Thermal resistance inside the duct
85 | U | Constant from IEC6028721 clause4272 |  | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87
86 | V | Constant from IEC6028721 clause4272 |  | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312
87 | Y | Constant from IEC6028721 clause4272 |  | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037 | 0.0037
88 | θm | Mean temperature of the medium in conduit | [°C] | 61.5287 | 66.1142 | 66.6758 | 66.6473 | 66.1148 | 61.5552
89 | Deq | Equivalent diameter of the cables inside the conduit | [mm] | 137.6 | 137.6 | 137.6 | 137.6 | 137.6 | 137.6
90 | T₄' | Thermal resistance of the medium in conduit | [K.m/W] | 0.22194 | 0.21596 | 0.21525 | 0.21528 | 0.21596 | 0.22191
Thermal resistance of the duct
91 | Do | Outer diameter of the conduit | [mm] | 225 | 225 | 225 | 225 | 225 | 225
92 | Di | Inner diameter of the conduit | [mm] | 200 | 200 | 200 | 200 | 200 | 200
93 | ρT | Thermal resistivity of the conduit material | [K.m/W] | 6 | 6 | 6 | 6 | 6 | 6
94 | T₄'' | Thermal resistance of the conduit | [K.m/W] | 0.11247 | 0.11247 | 0.11247 | 0.11247 | 0.11247 | 0.11247
Thermal resistance of the external medium
95 | L | Depth of cable/conduit axis | [m] | 1.1588 | 1.1588 | 1.1588 | 1.1588 | 1.1588 | 1.1588
96 | De / Do | External diameter of the cable conduit | [m] | 0.225 | 0.225 | 0.225 | 0.225 | 0.225 | 0.225
97 | u | Geometric factor as per IEC60287-2-1 clause 4.2.2 |  | 10.3004 | 10.3004 | 10.3004 | 10.3004 | 10.3004 | 10.3004
98 | ρTs | Thermal resistivity of the soil | [K.m/W] | 1.2249 | 1.2099 | 1.2052 | 1.205 | 1.21 | 1.2242
99 | Dx | Fictitious diameter at which the heat flows steadily as per Neher-Mc-Grath | [m] | 0.211 | 0.211 | 0.211 | 0.211 | 0.211 | 0.211
100 | ln(utr) | Geometric factor of the transient component of the heat flow as per Neher-Mc-Grath |  | 0 | 0 | 0 | 0 | 0 | 0
101 | µ | Effective loss load factor |  | 0.47434 | 0.47326 | 0.47418 | 0.47421 | 0.47326 | 0.47431
102 | T₄'''self | Thermal resistance of the cable isolated | [K.m/W] | 0.27954 | 0.2755 | 0.27495 | 0.27491 | 0.27551 | 0.27937
103 | T₄'''mutual | Thermal resistance associated to the temperature rise due to surrounding heat sources | [K.m/W] | 0.52261 | 0.55763 | 0.68947 | 0.69217 | 0.55764 | 0.52051
104 | Δθint | Temperature rise due to surrounding heat sources | [°C] | 15.0474 | 18.0553 | 20.1835 | 20.2002 | 18.0556 | 15.0339
105 | T₄''' | Thermal resistance of the external medium | [K.m/W] | 0.80215 | 0.83313 | 0.96442 | 0.96708 | 0.83315 | 0.79989
Thermal Capacitance IEC 853-2
106 | Q Conductor | Thermal capacitance | [J/m.K]
107 |  | Thermal capacitance equation
108 |  | Material surface | [mm²] | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
109 |  | Volumetric specific heat of the material | [J/(K*m³)] | 3450000 | 3450000 | 3450000 | 3450000 | 3450000 | 3450000
110 | Q Conductor Shield | Thermal capacitance | [J/m.K]
111 |  | Thermal capacitance equation
112 |  | External diameter | [mm] | 57.8 | 57.8 | 57.8 | 57.8 | 57.8 | 57.8
113 |  | Internal diameter | [mm] | 56.2 | 56.2 | 56.2 | 56.2 | 56.2 | 56.2
114 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
115 | Q1 Insulation | Thermal capacitance | [J/m.K]
116 |  | Thermal capacitance equation
117 |  | External diameter | [mm] | 93.8 | 93.8 | 93.8 | 93.8 | 93.8 | 93.8
118 |  | Internal diameter | [mm] | 57.8 | 57.8 | 57.8 | 57.8 | 57.8 | 57.8
119 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
120 | Q2 Insulation | Thermal capacitance | [J/m.K]
121 |  | Thermal capacitance equation
122 |  | External diameter | [mm] | 93.8 | 93.8 | 93.8 | 93.8 | 93.8 | 93.8
123 |  | Internal diameter | [mm] | 57.8 | 57.8 | 57.8 | 57.8 | 57.8 | 57.8
124 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
125 | Q Insulation Screen | Thermal capacitance | [J/m.K]
126 |  | Thermal capacitance equation
127 |  | External diameter | [mm] | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4
128 |  | Internal diameter | [mm] | 93.8 | 93.8 | 93.8 | 93.8 | 93.8 | 93.8
129 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
130 | Q Water Barrier Tape | Thermal capacitance | [J/m.K]
131 |  | Thermal capacitance equation
132 |  | External diameter | [mm] | 99 | 99 | 99 | 99 | 99 | 99
133 |  | Internal diameter | [mm] | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4
134 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
135 | Q Sheath | Thermal capacitance | [J/m.K]
136 |  | Thermal capacitance equation
137 |  | Material surface | [mm²] | 914.8318 | 914.8318 | 914.8318 | 914.8318 | 914.8318 | 914.8318
138 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2500000 | 2500000 | 2500000 | 2500000 | 2500000 | 2500000
139 | Q Jacket | Thermal capacitance | [J/m.K]
140 |  | Thermal capacitance equation
141 |  | External diameter | [mm] | 132 | 132 | 132 | 132 | 132 | 132
142 |  | Internal diameter | [mm] | 124 | 124 | 124 | 124 | 124 | 124
143 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
144 | Q Nylon 12 | Thermal capacitance | [J/m.K]
145 |  | Thermal capacitance equation
146 |  | External diameter | [mm] | 133.6 | 133.6 | 133.6 | 133.6 | 133.6 | 133.6
147 |  | Internal diameter | [mm] | 132 | 132 | 132 | 132 | 132 | 132
148 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
149 | Q Outer Jacket | Thermal capacitance | [J/m.K]
150 |  | Thermal capacitance equation
151 |  | External diameter | [mm] | 137.6 | 137.6 | 137.6 | 137.6 | 137.6 | 137.6
152 |  | Internal diameter | [mm] | 133.6 | 133.6 | 133.6 | 133.6 | 133.6 | 133.6
153 |  | Volumetric specific heat of the material | [J/(K*m³)] | 2400000 | 2400000 | 2400000 | 2400000 | 2400000 | 2400000
Ampacity
154 | T₄ | Total external thermal resistance | [K.m/W] | 1.1366 | 1.1616 | 1.2921 | 1.2948 | 1.1616 | 1.1343
155 | I | Cable core ampacity | [A] | 1500 | 1500 | 1500 | 1500 | 1500 | 1500

## Short Circ...- 1C132KV2000MM2CU
Cable Short Circuit
CYMCAP Version |  | 9.0 1 Revision
Cable Title |  | 1c 132kV 2000mm2 Cu
Date: |  | smoketest_single_backfill
2026-01-01 00:00:00
Symbol | Description |  | Unit | Circuit No. 1
| Cable Equipment ID |  |  | 1C132KV2000MM2CU
|  |  |  | Conductor |  |  | Sheath
|  |  |  | A | B | C | A | B | C
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483 | 147.7945 | 147.7945 | 147.7945
S | Layer Cross-Sectional Area |  | [mm²] | 2000 | 2000 | 2000 | 991.6123 | 991.6123 | 991.6123
θi | Initial Temperature |  | [°C] | 82.9393 | 88.4227 | 88.3083 | 67.6569 | 72.915 | 72.8056
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529 | 228.139 | 228.139 | 228.139
θf | Final Temperature |  | [°C] | 250 | 250 | 250 | 150 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 928050.3856 | 909060.9085 | 909457.6668 | 229671.6919 | 221279.5286 | 221455.8753
Inad | Non Adiabatic Short Circuit Current |  | [A] | 929410.5148 | 910393.2071 | 910790.5469 | 232706.5269 | 224203.4713 | 224382.1482
Symbol | Description |  | Unit | Circuit No. 2
| Cable Equipment ID |  |  | 1C132KV2000MM2CU
|  |  |  | Conductor |  |  | Sheath
|  |  |  | A | B | C | A | B | C
t | Short Circuit Time |  | [s] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
K | Current Carrying Component Material Constant |  | [As¹/₂ / mm²] | 225.6483 | 225.6483 | 225.6483 | 147.7945 | 147.7945 | 147.7945
S | Layer Cross-Sectional Area |  | [mm²] | 2000 | 2000 | 2000 | 991.6123 | 991.6123 | 991.6123
θi | Initial Temperature |  | [°C] | 88.2592 | 88.4233 | 82.9866 | 72.7584 | 72.9156 | 67.7023
β | Reciprocal of temperature coefficient at 0°C |  | [K] | 234.4529 | 234.4529 | 234.4529 | 228.139 | 228.139 | 228.139
θf | Final Temperature |  | [°C] | 250 | 250 | 250 | 150 | 150 | 150
Iad | Adiabatic Short Circuit Current |  | [A] | 909628.1281 | 909058.749 | 927886.8658 | 221531.8017 | 221278.5682 | 229599.9925
Inad | Non Adiabatic Short Circuit Current |  | [A] | 910961.258 | 910391.0445 | 929246.7553 | 224459.0779 | 224202.4983 | 232633.8801